Building Structured Cabling System

Request For Proposal

Modular master document to be tailored according to the requirements for the considered project

Prepared for

Cat.n / Class m – x/xTP copper sub-systems

&

Oyn fibre sub-system

Tenderbook V3.1 updated 09/2024

Instructions for use of the Aginode modular building tender document

The present modular building Request For Proposal (RFP)  master document shall be adapted by the user according to his project.

Every chapters to all tender types are included – The user shall review and tailor it according to his own needs.

All possible versions are contained into this document.

Using the outline mode of MS word the content of the document can be reduced to the main chapter heads or be expanded level by level (see user guide).

Deleting the head of a chapter/subchapter in the outline mode also remove the whole content of this chapter and MS Word automatically update the numbering of the remaining chapters.

The process begins at the main chapters (first) level. The complete useless chapters are removed (select and delete).

The list is than expanded to the next level and the sub-chapters of the second level that are not needed are deleted.

The process is going to continue down to the fully expanded document.

Please be aware that a second modular RFP document dedicated to Data Centre projects is also available.

The current page and all instruction texts highlighted in yellow

are to be deleted before publishing of the RFP doc.
Table of Contents

1.	Standards & Regulations	5

2.	Compliance to European Construction Product Regulation (CPR)	5

3.	Copper sub-system	8

3.1.	Cat.6 copper sub-system	8

3.2.	Cat.6A copper sub-system	8

3.3.	Cat.7A copper sub-system	9

4.	Fibre sub-system	10

4.1.	OM3 bend insensitive (BIMMF) fibre sub-system	10

4.2.	OM4 bend insensitive (BIMMF) fibre sub-system	11

4.3.	OM5 bend insensitive (BIMMF) fibre sub-system	12

4.4.	OS2 bend insensitive (BI) fibre sub-system	14

5.	Horizontal Cabling	16

5.1.	Copper Horizontal distribution cable	16

5.2.	Fibre horizontal distribution cable	29

5.3.	Modular RJ45 Jack	29

5.4.	RJ45 Field terminable Plug (MPTL)	35

5.5.	Telecom Outlets (TO)	36

5.6.	OF Telecommunications outlet	38

5.7.	Consolidation point	40

5.8.	Plug/jack pre-terminated assemblies (CP links)	44

5.9.	Optical fibre CP links	45

5.10.	24 port modular copper Patch Panels	46

5.11.	Copper Patch cords	52

5.12.	Link and Channel performance	64

6.	Intra-Building Backbone Cabling	68

6.1.	Optical Fibre	68

6.2.	Fibre pre-terminated cable assembly	71

6.3.	OF cable	74

6.4.	Optical Fibre Patch Panel	83

6.5.	Maxistrip Optical Fibre pigtails	105

6.6.	Tight Buffer Optical Fibre pigtails	107

6.7.	OM3 & OM4 BIMMF Optical Fibre Patch cords	109

6.8.	OS2 BI Optical Fibre Patch cords	111

6.9.	UHD bend insensitive LC OF Patch cords	113

6.10.	Secure Lock LC port blockers	115

7.	Inter-Building Backbone Cabling	116

7.1.	Optical Fibre	116

7.2.	OF cable	116

7.3.	Optical Fibre Patch Panel	116

7.4.	Optical Fibre pigtails	116

7.5.	Optical Patch cords	116

8.	Earthing requirements	116

9.	Testing	117

9.1.	Data Copper Testing	117

9.2.	Fibre testing	117

10.	Procedures	119

10.1.	Installation Guide	119

10.2.	Fire Protection	119

10.3.	Earthing	119

11.	Management of the Project	119

11.1.	Design of the Project and labelling	119

11.2.	Project Management	119

12.	Warranty	120

12.1.	Copper sub-system	120

12.2.	Fibre sub-system	121

13.	Documentation	124

13.1.	Response inclusions to the bid price	124

13.2.	During the Presentation of the Offer	124

13.3.	Kick-off of the Project	124

13.4.	On completion of the installation	124

Table of content update: When the creation of your RFP document is completed, please right-click into the table of content and choose ‘update field’ and select the ‘update entire table’ option.

# Standards & Regulations

This Request For Proposal (RFP) provides a description for a generic structured cabling system based on the latest edition of the applicable standards:

- ISO/IEC 11801: 2017 Ed.3 and subsequent addendums and revisions

or

- EN 50173-1 to -3:2018 and subsequent addendums and revisions

- EN50174-1:2018 / EN50174-2:2018 / EN50174-3:2013/A1:2017 and subsequent addendums and revisions

The object of this RFP is to define the structured cabling independently of the applications, which it is capable of supporting.

Furthermore, to allow for future demands, the cabling system must be easy to expand and maintain.

The successful vendor shall meet or exceed all requirements for the cabling system described in

this document.

The Cabling system installation shall be realized in accordance with the recommendations made in

the relevant standards, manufacturer’s recommendations and/or best industry practices.

# Compliance to European Construction Product Regulation (CPR)

Background information

Started as a Directive in 1989 (“CPD”) and turned into a Regulation in 2011 (“CPR”) which became applicable from 01st July 2013, the CPR was brought to life by the European Commission to enforce that construction works be designed and executed so as not to endanger the safety of persons, domestic animals or property nor damage the environment.

The goals of the CPR were:

- To define harmonised rules for marketing of construction products within the EU.

- To provide a common technical language to assess performance of construction products.

- To ensure availability of reliable information to allow comparison of construction products from different manufacturers in different countries.

EN 50575 is the harmonised European standard, issued in 2014 and published in the Official Journal of the European Union (OJEU) on 10th July 2015, which specifies requirements for cables used in permanent constructions with regard to their reaction to fire.

The fire performance of cables is classified based on a number of criteria:

- Flame spread and heat release

- Smoke production, acidity and flaming droplets

These criteria and test methods are specified in existing standards IEC/EN 60332-1, IEC/EN 61034-2, IEC/EN 60754-2 and in a new harmonised European standard EN 50399.

Cable performance classes

- 7 Euroclasses for flame spread and heat release: Aca, B1ca, B2ca, Cca, Dca, Eca and Fca (Aca being the most severe i.e. non-combustible and Fca having no criteria specified)

- 3 classifications and 2 sub-classes for smoke production: s1, s1a, s1b, s2, s3 (s1a being the most severe and s3 no criteria specified or failing any of the other four classifications)

- 3 classifications for acidity: a1, a2, a3 (a1 being the most severe and a3 no criteria specified or failing any of the other two classifications)

- 3 classifications for flaming droplets: d0, d1, d2 (d0 being the most severe and d2 no criteria specified or failing any of the other two classifications)

Requirements are going to depend on various parameters such as the type of building, the level of occupation, the difficulty of evacuation, etc. As building designs and operational rules will differ,

these requirements are not harmonised and therefore may vary from country to country.

It is the legal obligation of each EU Member State government to adopt CPR in national regulation, define the cable performance class and to guarantee effective surveillance of its market.

The company who place the product on the market in the EU is responsible to comply with the CPR obligations. This is either the actual manufacturer or the importer.

The product needs to have a Declaration of Performance (DoP)

This is a document drawn up by the manufacturer (or importer) in the language(s) required by the EU country where the product is made available and containing defined information such as product identification, its intended use, its declared performance according to CPR and the identification of the Notified Body. The DoP needs to be made publicly available, either on paper or in electronic format. It does not need to accompany the product itself.

The product packaging needs to have defined labelling including CE marking

labels on cable drums and boxes need to contain the same data as on the DoP, the reference number of the DoP, the CE mark and the year in which the CE marking was first affixed. The language of the label information can be chosen by the manufacturer (or importer). The cable itself does not need to bear the CE marking nor contain any other of the CPR requirements for labelling.

The cable manufacturer is not the solely responsible for CPR compliance. Also Distributors, Specifiers and Building Owners also bear responsibilities.

- Distributors should not resell cables (which they bought after the 1st of July 2017) for which there is no DoP and which do not bear the appropriate labelling.

- Specifiers must reference appropriate Euroclasses and s/a/d criteria according to national CPR regulations.

- Building owners need to ensure that the infrastructure on their building plans is in line with national CPR regulations.

Applicability

The regulation came into force from the 1st of July 2017, date when CE marking for CPR became mandatory.

As a consequence the bidder shall only propose copper and fibre cables that are compliant to the CPR.

Example of mandatory drum labelling:

For the purpose of this tender CPR marking on the cables jacket is mandatory

Example of mandatory print legend:

For each cable listed in this document and to be installed in the customer Data Centre and/or premises the Euroclass selected is clearly defined in the following pages according to the type of building, the level of occupation, the difficulty of evacuation, etc. as defined by the government of the country in which the cabling has to be installed (Requirements may vary from country to country).

All cables installed on this project, Copper, fibre and associated patch cords will be of Low

Smoke Zero Halogen construction complying with IEC 61034-1& 2 (smoke density test)  and IEC 60754-2 (acidity and conductivity test). Plenum rated cables will not be installed.

Notes

Please select the appropriate Euroclass in every chapter when needed (Delete the wrong ones).

# Copper sub-system

## Cat.6 copper sub-system

This Tender document covers the design, supply, installation, testing and commissioning of a Category 6 cabling system.

Tenderers shall propose and submit a Category 6 universal cabling system which will function for voice, data and LAN communications, for video applications etc.

The cabling system is also open to new applications which require a Class E / Cat 6 cabling system as defined in the latest editions of the standards: ISO/IEC 11801:2017 or EN 50173:2018.

The terminology and references in this document as well as the Link/Channel Performance figures for Class EA are based on ISO/IEC 11801:2017 or EN 50173:2018.

The data sheets and warranty modules showing the features and the guaranteed values compliant to the requirements of this RFP will be attached by the vendor to his tender documents.

All proposed components including the patch cords have to be produced by the same manufacturer. This issue will ensure that a « Class E Channel Warranty » can be obtained from the manufacturer.

## Cat.6A copper sub-system

This Tender document covers the design, supply, installation, testing and commissioning of a Category 6A cabling system.

Tenderers shall propose and submit a Category 6A universal cabling system which will function for voice, data and LAN communications, for video applications etc.

The cabling system is also open to new applications which require a Class EA / Cat 6A cabling system as defined in the latest editions of the standards: ISO/IEC 11801:2017 or EN 50173:2018.

The terminology and references in this document as well as the Link/Channel Performance figures for Class EA are based on ISO/IEC 11801:2017 or EN 50173:2018.

The data sheets and warranty modules showing the features and the guaranteed values compliant to the requirements of this RFP will be attached by the vendor to his tender documents.

All proposed components including the patch cords have to be produced by the same manufacturer. This issue will ensure that a « Class EA Channel Warranty » can be obtained from the manufacturer.

## Cat.7A copper sub-system

This Tender document covers the design, supply, installation, testing and commissioning of a Category 7A cabling system.

Tenderers shall propose and submit a Category 7A universal cabling system which will function for voice, data and LAN communications, for video applications etc.

The cabling system is also open to new applications which require a Class FA / Cat 7A cabling system as defined in the latest editions of the standards: ISO/IEC 11801:2017 or EN 50173:2018.

The terminology and references in this document as well as the Link/Channel Performance figures for Class EA are based on ISO/IEC 11801:2017 or EN 50173:2018.

The data sheets and warranty modules showing the features and the guaranteed values compliant to the requirements of this RFP will be attached by the vendor to his tender documents.

All proposed components including the patch cords have to be produced by the same manufacturer. This issue will ensure that a « Class FA Channel Warranty » can be obtained from the manufacturer.

# Fibre sub-system

The optical fibre backbone shall be capable of providing the bandwidth required by the use of a the horizontal cabling solution defined in the former chapter 3.

## OM3 bend insensitive (BIMMF) fibre sub-system

This Tender document covers the design, supply, installation, testing and commissioning of an OM3 BIMMF (Ben Insensitive Multimode Fibre) cabling sub-system.

The fibre systems shall be warranted to support any current or future application designed to be supported

by OM3 fibres according to IEC 60793-2-10 A1a.2b.

BIMMF fibres are designed to withstand tight bends with substantially less signal loss than traditional multimode fibre.

The cabling system is also open to new applications which require an OM3 cabling sub-system as defined in the latest editions of the standards: ISO/IEC 11801: 2017 or EN 50173:2018.

Effective modal bandwidth (EMB) of OM3 fibres shall be measured according to the templates method of IEC 60793-2-10 section D2 and the calculated effective modal bandwidth of IEC 60793-2-10 ed.4 section D3.

The data sheets and warranty modules showing the features and the guaranteed values compliant to the requirements of this RFP will be attached by the vendor to his tender documents.

All proposed components including the connectors, pigtails and patch cords have to be produced by the same manufacturer. This issue will ensure that the applications and the distance support Warranty as described in the Warranty chapter of this RFP can be obtained from the manufacturer.

Guaranteed distances

## OM4 bend insensitive (BIMMF) fibre sub-system

This Tender document covers the design, supply, installation, testing and commissioning of an OM4 BIMMF (Ben Insensitive Multimode Fibre) cabling sub-system.

The fibre systems shall be warranted to support any current or future application designed to be supported

by OM4 fibres according to IEC 60793-2-10 A1a.3b.

BIMMF fibres are designed to withstand tight bends with substantially less signal loss than traditional multimode fibre.

The cabling system is also open to new applications which require an OM4 cabling sub-system as defined in the latest editions of the standards: ISO/IEC 11801: 2017 or EN 50173:2018.

Effective modal bandwidth (EMB) of OM4 fibres shall be measured according to the templates method of IEC 60793-2-10 section D4 and the calculated effective modal bandwidth of IEC 60793-2-10 de.4 section D5.

The data sheets and warranty modules showing the features and the guaranteed values compliant to the requirements of this RFP will be attached by the vendor to his tender documents.

All proposed components including the connectors, pigtails and patch cords have to be produced by the same manufacturer. This issue will ensure that the applications and the distance support Warranty as described in the Warranty chapter of this RFP can be obtained from the manufacturer.

Guaranteed distances

## OM5 bend insensitive (BIMMF) fibre sub-system

This Tender document covers the design, supply, installation, testing and commissioning of an OM5 cabling sub-system.

The fibre systems shall be warranted to support any current or future application designed to be supported

by OM5 fibres according to IEC 60793-2-10 A1a.4b.

The cabling system is also open to new applications which require an OM5 cabling sub-system as defined in the latest editions of the standards: ISO/IEC 11801: 2017 or EN 50173:2018.

BI  fibres are designed to withstand tight bends with substantially less signal loss than traditional singlemode fibre.

Effective modal bandwidth (EMB) of OM4 fibres shall be measured according to the templates method of IEC 60793-2-10 section D4 and the calculated effective modal bandwidth of IEC 60793-2-10 section D5.

The data sheets and warranty modules showing the features and the guaranteed values compliant to the requirements of this RFP will be attached by the vendor to his tender documents.

All proposed components including the connectors, pigtails and patch cords have to be produced by the same manufacturer. This issue will ensure that the applications and the distance support Warranty as described in the Warranty chapter of this RFP can be obtained from the manufacturer.

Guaranteed distances

## OS2 bend insensitive (BI) fibre sub-system

This Tender document covers the design, supply, installation, testing and commissioning of a BI OS2 cabling sub-system.

The fibre systems shall be warranted to support any current or future application designed to be supported

By Bend Insensitive Singlemode G657.A1 fibres.

The BI OS2 fibre shall be compliant to the IEC 60793-2-50 standard as fibre type B6.a1.

BI  fibres are designed to withstand tight bends with substantially less signal loss than traditional singlemode fibre.

The cabling system is also open to new applications which require an OS2 cabling sub-system as defined in the latest editions of the standards: ISO/IEC 11801: 2017 or EN 50173:2018.

The data sheets and warranty modules showing the features and the guaranteed values compliant to the requirements of this RFP will be attached by the vendor to his tender documents.

All proposed components including the connectors, pigtails and patch cords have to be produced by the same manufacturer. This issue will ensure that the applications and the distance support Warranty as described in the Warranty chapter of this RFP can be obtained from the manufacturer.

Guaranteed distances

# Horizontal Cabling

## Copper Horizontal distribution cable

### Cat.6 U/UTP cable

The horizontal 4 pair cable shall be Category 6 U/UTP to meet the quality and performance criteria necessary to ensure correct operation of the installation for frequencies up to 350 MHz and compliance with the warranty.

The installation design and routing of all cables shall take account of the manufacturer limits for the continued performance of the cables and the compliance with the warranty.

The cable shall be a 4 twisted pair cable with AWG 23 conductors. Having an external sheathing in a material that does not give off toxic fumes (Zero Halogen) in case of fire and offer flame propagation retardant properties. The cable shall be compliant to the IEC 60332-1 standard.

Traceability numbers should accompany the cable supplied from the manufacturers packaging to assist in quality validation of the installed cable.

In the construction of the cable cross-talk performance shall be maintained using a C³ (Central dielectric Cross-talk Cancellation) member set between the 4 pairs.

All pairs must have a fitted impedance of 100 Ohms, with a tolerance of +/- 5 Ohms.

Conductor pairs shall be identified by insulation utilising standardised colour code (Blue/White, Orange/White, Green/White, Brown/White).

The Cat.6 cable shall comply to the following electrical performances up to 350 MHz.

Max. And Min. Values shall be warranted by the manufacturer.

#### CPR grade compliance requirement (Eca)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Eca and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Eca)

Example of product

LANmark-6 U/UTP Cat 6 LSZH Eca Orange 500m reel

Aginode reference: N100.605-OE

#### CPR grade compliance requirement (Dca s2,d2,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Dca s2,d2,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Dca s2,d2,a1)

Example of product

LANmark-6 U/UTP Cat 6 LSZH Dca s2 d2 a1 Orange 500m reel

Aginode reference: N100.605-OD

#### CPR grade compliance requirement (Cca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1a,d1,a1)

Example of product

LANmark-6 U/UTP Cat 6 LSZH Cca s1a d1 a1 Orange 500m reel

Aginode reference: N100.605-OC

### Cat.6 F1/UTP cable

The horizontal 4 pair cable shall be Category 6 F1/UTP to meet the quality and performance criteria necessary to ensure correct operation of the installation for frequencies up to 350 MHz and compliance with the warranty.

The installation design and routing of all cables shall take account of the manufacturer limits for the continued performance of the cables and the compliance with the warranty.

The cable shall be a 4 twisted pair cable with AWG 24 conductors. Having an external sheathing in a material that does not give off toxic fumes (Zero Halogen) in case of fire and offer flame propagation retardant properties. The cable shall be compliant to the IEC 60332-1 standard.

Traceability numbers should accompany the cable supplied from the manufacturers packaging to assist in quality validation of the installed cable.

In the construction of the cable cross-talk performance shall be maintained using a C³ (Central dielectric Cross-talk Cancellation) member set between the 4 pairs.

All pairs must have a fitted impedance of 100 Ohms, with a tolerance of +/- 5 Ohms.

Conductor pairs shall be identified by insulation utilising standardised colour code (Blue/White, Orange/White, Green/White, Brown/White).

The cable shall contain 1 foil screen. The foil shall have the metallic side facing outwards, allowing the cable to be automatically grounded during the termination process without having to fold back the foil. This will provide instant 360° grounding contact to ensure immunity from Alien Crosstalk and other external interference.

A tinned copper drain wire, shall be sandwiched between the screen and the external sheathing.

The Cat.6 cable shall comply to the following electrical performances up to 350 MHz.

Max. And Min. Values shall be warranted by the manufacturer.

#### CPR grade compliance requirement (Dca s2,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Dca s2,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Dca s2,d1,a1)

Example of product

LANmark-6 F1/UTP Cat 6 LSZH Dca s2 d1 a1 Orange 1000m reel

Aginode reference: N100.622-OD

#### CPR grade compliance requirement (Cca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1a,d1,a1)

Example of product

LANmark-6 F1/UTP Cat 6 LSZH Cca S1a d1 a1 Orange 1000m reel

Aginode reference: N100.622-OC

### Cat.6A F1/UTP cable

The horizontal 4 pair cable shall be Category 6A F1/UTP to meet the quality and performance criteria necessary to ensure correct operation of the installation for frequencies up to 500 MHz and to ensure the compliance with the warranty.

The installation design and routing of all cables shall take account of the manufacturer limits for the continued performance of the cables and the compliance with the warranty.

The cable shall be a 4 twisted pair cable with AWG 23 plain copper conductors and shall have an external sheathing in a material that does not give off toxic fumes (Zero Halogen) in case of fire and offer flame propagation retardant properties. The cable shall be compliant to the IEC 60332-1 standard.

Traceability numbers should accompany the cable supplied from the manufacturers packaging to assist in quality validation of the installed cable.

In order to provide alien cross-talk (AXT) immunity for 10 GBASE-T Ethernet transmission, the use of screened cable is mandatory.

In the construction of the cable NEXT performance shall be maintained using a C³ (Central dielectric Cross-talk Cancellation) member set between the 4 pairs.

All pairs must have a fitted impedance of 100 Ohms, with a tolerance of +/- 5 Ohms.

Conductor pairs shall be identified by insulation utilising standardised colour code (Blue/White, Orange/White, Green/White, Brown/White).

The cable shall contain 1 foil screen. The foil shall have the metallic side facing outwards, allowing the cable to be automatically grounded during the termination process without having to fold back the foil. This will provide instant 360° grounding contact to ensure immunity from Alien Crosstalk and other external interference.

A tinned copper drain wire, shall be provided between the aluminium screen and the external sheathing.

The Cat.6A cable shall comply to the following electrical performances.

Max. And Min. Values shall be warranted by the manufacturer.

#### CPR grade compliance requirement (Dca s2,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Dca s2,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Dca s2,d1,a1)

Example of product

LANmark-6A F1/UTP AWG23 Cat 6A LSZH Dca s2 d1 a1 Orange 1000m reel

Aginode reference: N100.622G-OD

#### CPR grade compliance requirement (Cca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class CCA s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1a,d1,a1)

Example of product

LANmark-6A F1/UTP AWG23 Cat 6A LSZH Cca s1a d1 a1 Orange 1000m reel

Aginode reference: N100.622G-OC

### Cat.6A F/FTP cable

The horizontal 4 pair cable shall be Category 6A F/FTP to meet the quality and performance criteria necessary to ensure correct operation of the installation for frequencies up to 500 MHz and to ensure the compliance with the warranty.

The installation design and routing of all cables shall take account of the manufacturer limits for the continued performance of the cables and the compliance with the warranty.

The cable shall be a 4 twisted pair cable with AWG 23 plain copper conductors and shall have an external sheathing in a material that does not give off toxic fumes (Zero Halogen) in case of fire and offer flame propagation retardant properties. The cable shall be compliant to the IEC 60332-1 standard.

Traceability numbers should accompany the cable supplied from the manufacturers packaging to assist in quality validation of the installed cable.

In order to provide alien cross-talk (AXT) immunity for 10 GBASE-T Ethernet transmission, the use of screened cable is mandatory.

This high performance cable shall have an individual and a common screen construction to ensure immunity from Alien Crosstalk and other external interference up to 500 MHz.

All four pairs shall be individually screened with an aluminium foil.

The overall cable shall be screened with a complementary aluminium foil.

All pairs must have a fitted impedance of 100 Ohms, with a tolerance of +/- 5 Ohms.

Conductor pairs shall be identified by insulation utilising standardised colour code (Blue/White, Orange/White, Green/White, Brown/White).

The Cat.6A cable shall comply to the following electrical performances.

Maximum and Minimum values shall be warranted by the manufacturer.

#### CPR grade compliance requirement (Dca s2,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Dca s2,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Dca s2,d1,a1)

Example of product

LANmark-6A F/FTP AWG23 Cat 6A LSZH Dca s2 d1 a1 Orange 1000m reel

Aginode reference: N100.692G-OD

#### CPR grade compliance requirement (Cca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1a,d1,a1)

Example of product

LANmark-6A F/FTP AWG23 Cat 6A LSZH Cca s1 d1 a1 Orange 1000m reel

Aginode reference: N100.692G-OC

### Cat.7 S/FTP cable

The horizontal 4 pair cable shall be Category 7 S/FTP to meet the quality and performance criteria necessary to ensure correct operation of the installation for frequencies up to 600 MHz and compliance with the warranty.

The installation design and routing of all cables shall take account of the manufacturer limits for the continued performance of the cables and the compliance with the warranty.

The cable shall be a 4 twisted pair cable with AWG 23 plain copper conductors and shall have an external sheathing in a material that does not give off toxic fumes (Zero Halogen) in case of fire and offer flame propagation retardant properties. The cable shall be compliant to the IEC 60332-1 standard.

Traceability numbers should accompany the cable supplied from the manufacturers packaging to assist in quality validation of the installed cable.

This very high performance cable shall have an individual and a common screen construction to ensure immunity from Alien Crosstalk and other external interference up to 600 MHz.

All four pairs shall be individually screened with an aluminium foil.

The cable shall be shielded with a tinned copper braid.

All pairs must have a fitted impedance of 100 Ohms, with a tolerance of +/- 5 Ohms.

Conductor pairs shall be identified by insulation utilising standardised colour code (Blue/White, Orange/White, Green/White, Brown/White).

The Cat.7 cable shall comply to the following electrical performances up to 600 MHz.

Maximum and Minimum values shall be warranted by the manufacturer.

#### CPR grade compliance requirement (Cca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1a,d1,a1)

Example of product

LANmark-7 S/FTP 23AWG LSZH C s1a d1 a1 Orange 1000m Reel

Aginode reference: N100.65-OC

#### CPR grade compliance requirement (B2ca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class B2ca s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade B2ca s1a,d1,a1)

Example of product

LANmark-7 S/FTP 23AWG LSZH B2 s1a d1 a1 Orange 1000m Reel

Aginode reference: N100.365-OB

### Cat.7A S/FTP cable

The horizontal 4 pair cable shall be Category 7A S/FTP to meet the quality and performance criteria necessary to ensure correct operation of the installation for frequencies up to 1,250 MHz and compliance with the warranty.

It offers large headroom above the Cat 7A requirement. Due to this excellent electrical performance and positive ACR up to at least 1250MHz the cable supports the applications like 10GBASE-T as well as 25GBASE-T

The installation design and routing of all cables shall take account of the manufacturer limits for the continued performance of the cables and the compliance with the warranty.

The cable shall be a 4 twisted pair cable with AWG 23 plain copper conductors and shall have an external sheathing in a material that does not give off toxic fumes (Zero Halogen) in case of fire and offer flame propagation retardant properties. The cable shall be compliant to the IEC 60332-1 standard.

Traceability numbers should accompany the cable supplied from the manufacturers packaging to assist in quality validation of the installed cable.

This very high performance cable shall have an individual and a common screen construction to ensure immunity from Alien Crosstalk and other external interference up to 1250 MHz.

All four pairs shall be individually screened with an aluminium foil.

The cable shall be shielded with a tinned copper braid.

All pairs must have a fitted impedance of 100 Ohms, with a tolerance of +/- 5 Ohms.

Conductor pairs shall be identified by insulation utilising standardised colour code (Blue/White, Orange/White, Green/White, Brown/White).

The Cat.7A cable shall comply to the following electrical performances up to 1,250 MHz.

Maximum and Minimum values shall be warranted by the manufacturer.

#### CPR grade compliance requirement (Dca s2,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Dca s2,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Dca s2,d1,a1)

Example of product

LANmark-7A S/FTP Cat 7A 1250MHz 23AWG LSZH Dca s2 d1 a1 Orange 1000m Reel

Aginode reference: N100.371-OD

#### CPR grade compliance requirement (Cca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class CCA s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1a,d1,a1)

Example of product

LANmark-7A S/FTP Cat 7A 1250MHz 23AWG LSZH C s1a d1 a1 Orange 1000m Reel

Aginode reference: N100.371-OC

#### CPR grade compliance requirement (B2ca s1a,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class B2ca s1a,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade B2ca s1a,d1,a1)

Example of product

LANmark-7A S/FTP Cat 7A 1250MHz 23AWG LSZH B2 s1a d1 a1 Orange 1000m Reel

Aginode reference: N100.371-OB

## Fibre horizontal distribution cable

This optional chapter shall only be present if OF outlets (FTTD) are required. If not, please delete this chapter

OF horizontal distribution links (FTTD) are required in some areas of the facility.

The optical fibre cable shall consist of multimode OM3 / OM4 (Please keep only the fibre you want to use) fibre with colour coded fibre for identification.

The characteristics of the fibre type are described in the backbone chapter.

The cable shall be suitable for connector manufacturer field termination processes (SC or LC connectors) and for OF pigtails splicing.

a Tight Buffer cable including 2 to 24 fibres shall be be used. The cable shall be a dry construction i.e. with no gel content. The jacket material shall be waterproof LSZH with a minimum fire performance of IEC 332-3.

Every fibre shall be 900µm diameter secondary coated each being a different colour or suitably identified for termination identification.

The cable strength member shall be glass yarn laid longitudinally between the fibres and the inside wall of the outer jacket. The cable shall be dielectric construction, i.e. with no metallic content.

### Detailed product information (CPR grade Cca s1,d1,a1)

Example of product

LANmark-OF Tight Buffer Universal 12x Multimode 50/125 OM3 LSZH Cca S1 d1 a1 Aqua

Aginode reference: N165.TBUN12-AB

LANmark-OF Tight Buffer Universal 12x Multimode 50/125 OM4 LSZH Cca S1 d1 a1 Aqua

Aginode reference: N167.TBUN12-AB

## Modular RJ45 Jack

### Cat.6 unscreened connector

The connector shall be fully compliant to the IEC 60603-7-4 standard that defines the Cat.6 unscreened connector to be used to form a Class E channel as specified in the ISO/IEC 11801: Ed.3 standard.

The connector shall support PoE (IEEE 802.3af), PoE + (IEEE 802.3at) and PoE ++ (IEEE 802.3bt) applications and shall pass all the tests for PoE ++ requirements according to IEC 60512-99-002 Ed.1).

Each connector shall provide both T568A and T568B colour code identification for the IDC contacts at the rear of the connector. Termination is to be in accordance with the T568B colour code. Reassignment of pairs is forbidden.

All conductors from the 4 pair cable are to be terminated on the respective contacts.

To avoid installation errors, pair assignment in the wire organiser of the Snap-In jack must be identified using colours which match the cable pairs .

The Snap-In format of the connector shall make it compatible with the whole range of modular structural hardware including patch panels, outlets and CP boxes.

Optional clips shall be available to turn Snap-In into keystone format.

A table of compatibility indicating which clip shall be used to ensure compatibility with a large range of third party structural hardware shall be available from the manufacturer.

All RJ45 connectors shall be reusable. When the RJ45 connectors are to be reused, this shall be done in a safe and reliable way. For this reason, a tool specially developed by the manufacturer shall be used.

In the case of a 3 or 4 connector Channel with Consolidation Point (CP), a specific version of connector having IDC contacts suitable for the termination of stranded cable (ST) shall be used at the TO and/or at the presentation panel.

#### Detailed product information

Example of product

LANmark-6 Evo Snap-In Connector Category 6 Unscreened

Aginode reference: N420.660

LANmark-6 Evo Snap-In Connector Category 6 Unscreened Stranded Wire

Aginode reference: N420.661

### Cat.6 screened connector

The RJ45 connector shall be fully screened to ensure protection against EMI and for Alien cross-talk compliance. Connectors shall also provide termination facilities for the drain wire of some screened cable.

The connector shall support PoE (IEEE 802.3af), PoE + (IEEE 802.3at) and PoE ++ (IEEE 802.3bt) applications and shall pass all the tests for PoE ++ requirements according to IEC 60512-99-002 Ed.1).

The connector shall be fully compliant to the IEC 60603-7-5 standard that defines the Cat.6 screened connector to be used to form a Class E channel as specified in the ISO/IEC 11801: Ed.3 standard.

Each connector shall provide both T568A and T568B colour code identification for the IDC contacts at the rear of the connector. Termination is to be in accordance with the T568B colour code. Reassignment of pairs is forbidden.

All conductors from the 4 pair cable are to be terminated on the respective contacts.

To avoid installation errors, pair assignment in the wire organiser of the Snap-In jack must be identified using colours which match the cable pairs .

The Snap-In format of the connector shall make it compatible with the whole range of modular structural hardware including patch panels, outlets and CP boxes.

Optional clips shall be available to turn Snap-In into keystone format.

A table of compatibility indicating which clip shall be used to ensure compatibility with a large range of third party structural hardware shall be available from the manufacturer.

All RJ45 connectors shall be reusable. When the RJ45 connectors are to be reused, this shall be done in a safe and reliable way. For this reason, a tool specially developed by the manufacturer shall be used.

In the case of a 3 or 4 connector Channel with Consolidation Point (CP), a specific version of connector having IDC contacts suitable for the termination of stranded cable (ST) shall be used at the TO and/or at the presentation panel.

#### Detailed product information

Example of product

LANmark-6 Evo Snap-In Connector Category 6 Screened

Aginode reference: N420.666

LANmark-6 Evo Snap-In Connector Category 6Screened Stranded Wire

Aginode reference: N420.667

### Cat.6A screened connector

The RJ45 connector shall be fully screened to ensure protection against EMI and for Alien cross-talk compliance. Connectors shall also provide termination facilities for the drain wire of some screened cable.

The connector shall support PoE (IEEE 802.3af), PoE + (IEEE 802.3at) and PoE ++ (IEEE 802.3bt) applications and shall pass all the tests for PoE ++ requirements according to IEC 60512-99-002 Ed.1).

The connector shall be fully compliant to the IEC 60603-7-51 standard that defines the Cat.6A connector to be used to form a Class EA channel as specified in the ISO/IEC 11801: Ed.3 standard.

Each connector shall provide both T568A and T568B colour code identification for the IDC contacts at the rear of the connector. Termination is to be in accordance with the T568B colour code. Reassignment of pairs is forbidden.

All conductors from the 4 pair cable are to be terminated on the respective contacts.

To avoid installation errors, pair assignment in the wire organiser of the Snap-In jack must be identified using colours which match the cable pairs .

The Snap-In format of the connector shall make it compatible with the whole range of modular structural hardware including patch panels, outlets and CP boxes.

Optional clips shall be available to turn Snap-In into keystone format.

A table of compatibility indicating which clip shall be used to ensure compatibility with a large range of third party structural hardware shall be available from the manufacturer.

All RJ45 connectors shall be reusable. When the RJ45 connectors are to be reused, this shall be done in a safe and reliable way. For this reason, a tool specially developed by the manufacturer shall be used.

In the case of a 3 or 4 connector Channel with Consolidation Point (CP), a specific version of connector having IDC contacts suitable for the termination of stranded cable (ST) shall be used at the TO and/or at the presentation panel.

#### Detailed product information

Example of product

LANmark-6A Evo Snap-In Connector Category 6A 500MHz Screened for solid wire

Aginode reference: N420.66A

LANmark-6A Evo Snap-In Connector Category 6A 500MHz Screened for stranded wire

Aginode reference: N420.67A

### Cat.7A/Cat.8 screened connector

The GG45 connector shall be fully screened to ensure protection against EMI and for Alien cross-talk compliance. Connectors shall also provide termination facilities for the drain wire of some screened cable.

The connector shall support PoE (IEEE 802.3af), PoE + (IEEE 802.3at) and PoE ++ (IEEE 802.3bt) applications and shall pass all the tests for PoE ++ requirements according to IEC 60512-99-002 Ed.1).

The connector shall be fully compliant to the IEC 60603-7-71 and  IEC 60603-7-82 standard that defines the Cat.8.2 connector to be used to form a Class I/II channel as specified in the ISO/IEC 11801: 2017 ed.3 standard.

In particular, the connector shall contain a full Cat.6 (RJ45) interface as well as a full Cat.7A/Cat.8 interface using four additional contacts for 2000MHZ transmission.

It shall offer full backward compatibility with RJ45 plugs.

Each connector shall provide both T568A and T568B colour code identification for the IDC contacts at the rear of the connector. Termination is to be in accordance with the T568B colour code. Reassignment of pairs is forbidden.

All conductors from the 4 pair cable are to be terminated on the respective contacts.

To avoid installation errors, pair assignment in the wire organiser of the Snap-In jack must be identified using colours which match the cable pairs.

The Snap-In format of the connector shall make it compatible with the whole range of modular structural hardware including patch panels, outlets and CP boxes.

In the case of a 3 or 4 connector Channel with Consolidation Point (CP), a specific version of connector having IDC contacts suitable for the termination of stranded cable shall be used at the TO and/or at the presentation panel.

Electrical performances of the GG45 connector

#### Detailed product information

LANmark GG45 is a screened RJ45-compatible cable jack specified up to 2000MHz. It is designed specifically to support the high frequencies required for applications beyond 10 Gigabit Ethernet.

- Combined with LANmark-7A Cable and Patch Cords, GG45 offers support for 25GBase-T.

- Combined with a LANmark-8 2GHz cable, GG45 offers support for 40GBase-T.

Example of product

LANmark GG45 12C Snap-In Connector Cat.7A/8 2000MHz Screened

Aginode reference: N420.735

LANmark GG45 12C Snap-In Connector Cat.7A/8 2000MHz Screened for stranded wire

Aginode reference: N420.736

## RJ45 Field terminable Plug (MPTL)

MPTL are being used for direct data connections between patch panels and network devices, such as Wireless Access Points and IP Cameras, which are usually located in or near the ceiling void and often powered over the network via PoE.

The Cat.6A RJ45 plug shall be fully shielded, offering excellent coupling attenuation and immunity from Alien Crosstalk and other external interferences.

The plastic snap-on boot with reinforced strain relief and closing nut features an integrated latch protector.

The wire organiser shall ensure easy mounting of the Cat.6A Field Terminable Plug without the need for a special termination tool, apart from a pair of parallel jaw pliers.

The field Terminable Plug shall meet or exceed the requirements for Category 6A connecting hardware as described in ISO/IEC 11801, IEC 60603-7-51 and TIA 568.2-D. In conjunction with Cat.6A cable, the plug shall support MPTL configurations as specified in TIA 568.2-D and in the ISO/IEC TR 11801-9910 ED1.

Installations with Cat.6A cable and connectivity of the same manufacturer including the Cat.6A Field

Terminable Plug can qualify for a 25 year full system warranty, which includes Parts, Installation, Channel Performance and Application Support, as described in the Certified System Warranty of the manufacturer.

### Detailed product information

Example of product

LANmark-6A Field Terminable Plug Category 6A Screened

Aginode reference: N490.001

## Telecom Outlets (TO)

### European mounting hardware

All European format (45x45) outlets are fitted with removable shutters, which can be replaced by colour-coded shutters ( 8 colours) available from the manufacturer standard product range.

The presentation of the outlet shall provide for labelling and identification. A transparent window shall protect the labelling tag.

The choice between single and dual RJ45 outlet modules shall be provided.

The range shall include cover plates, flat and angled modules for Snap-In connectors and surface mount boxes.

#### Detailed product information

Example of product

LANmark EU style angled 45 x 45 module 1 Snap-In white

Aginode reference: N423.520

LANmark EU style angled 45 x 45 module 2 Snap-In white

Aginode reference: N423.540N

LANmark EU style 45 x 45 frame white

Aginode reference: N200.050

LANmark EU style 45 x 45 surface mount box white

Aginode reference: N200.116

### UK mounting hardware

All UK format outlets shall be either 50x50mm or 50x100mm “Euromod” style. Outlets shall have spring-loaded or removable shutters. The removable shutters can be replaced by coloured shutters ( red, green, blue, yellow) available from the manufacturer’s standard product range.

Each outlet is equipped with a labelling window or labelling surface.

Wall outlets shall accommodate one, two, three or four modules as required.

The range shall include cover plates, flat or angled modules for Snap-In connectors and surface mount boxes.

Outlets mounted in floor boxes or GOP modules shall utilise manufacturer approved mounting hardware appropriate for the performance category and cable type selected.

Outlet style can be country and project dependant. If a third party outlet style is requested for the project, the connector shall also fit in specific structural hardware for Snap-in format of third parties. If not available, the Snap-in connector can be used in combination with a keystone clip and specific structural hardware for keystone connectors.

A compatibility table with third party structural hardware should be available from the cabling manufacturer.

The outlet style is to be defined by the vendor according to the project specification.

#### Detailed product information

Example of product

UK Style 50 x 50 Frame Flat White

Aginode reference: N424.013

UK Style Backbox Single Gang White

Aginode reference: N424.532

LANmark UK Style Angled 50 x 50 Module 2 Snap-In White

Aginode reference: N423.540UN

Example of product

UK Style 100 x 50 Frame Flat White

Aginode reference: N424.023

LANmark UK Style Angled 50 x 50 Module 2 Snap-In White

Aginode reference: N423.540UN

Note

The double gang frame can be used horizontal or vertical

If vertical mounting is required, it needs to be noted that the Euromod ring (= adaption ring to go from 45x45 to 50x50 format), with which our UK 50x50 outlets are pre-equipped, needs to be turned 90° otherwise the outlet can’t be fixed in the frame.

Example of product

LANmark 86 x 86 Wallplate 1 Snap-In White

Aginode reference: N423.861

LANmark 86 x 86 Wallplate 2 Snap-In White

Aginode reference: N423.862

LANmark UK Style 25 x 50 Module 1 Snap-In White

Aginode reference: N424.310

## OF Telecommunications outlet

This optional chapter shall only be present if OF outlets (FTTD) are required. If not, please delete this chapter

The termination of the OF horizontal links shall be performed either into the standard outlet described in the former chapter using an OF patch cord or into a specific FO splicing outlet.

The two OF outlet ports fitted with removable shutters shall be compatible with the Snap-In format of the manufacturer. OF couplers (SC or LC) and RJ45 connectors shall have the same Snap-In format in order to ensure compatibility and offer mixed Cu/FO outlets.

Splicing Telecom Outlet shall be designed for robust Fibre To The Desk applications. The outlet combines the benefits of the Snap-In concept with full flexibility of termination methods: direct, splicing with aluminium protections and splicing with heat shrink protections.

The fully loaded Outlet shall support up to 2 fibres when working with SC Snap-In couplers and up to 4 fibres when working with LC Snap-In couplers.

The OF Telecom Outlet shall provide management for 50 cm of fibre per link after breaking the fibres out from the cable.

In the OF Outlet, the fibres have to be wired in such a way that the dual OF channel polarity is maintained. Wiring of the fibres has to be done according to the guidelines provided by the manufacturer.

The presentation of the outlet shall provide for labelling and identification. A transparent window shall protect the labelling tag.

A fibre optic version of the Zone Distribution box (CP box) shall also be available for FTTD applications.

OF patch panels are described further in the backbone chapter.

#### Detailed product information

Example of product

Modular OF Splicing Outlet 45X45 for 2 Snap-in adaptors

Aginode reference: N420.035

## Consolidation point

### Zone Distribution box

for the installation of a consolidation point (CP), a Zone Distribution box (ZD box) significantly improves the flexibility of desk location in the offices. It is particularly useful in an open office where the flexibility of relocating outlets in the work area is required.

The ZD box shall be compatible with all Snap-In connectors and shall have the following features:

- Two versions: 6 or 12 shuttered pre-numbered ports.

- Earthing and/or mass contact features

- Back entry: two pre-perforated openings at the back side

- Bottom entry on the base allow cable entry from different sides (12 port version only).

- Foam protection against dust on back side.

- Tie wrap features for cable fixing

ZD boxes shall be easy to install on walls, under raised floors or in ceiling voids, due to their multiple mounting features.

Optional coloured shutters need to be available to easily indicate different services when required.

A fibre version of this copper ZD box shall be available.

The fibre version shall be design to be equipped with optional splice trays.

The cable entry shall be designed to accommodate pre-terminated assemblies equipped with cable glands.

#### Detailed product information

Example of product

LANmark ZD box 12 Snap-In White

Aginode reference: N521.600

LANmark ZD box 6 Snap-In White

Aginode reference: N521.606

LANmark ZD box 12 Snap-In White

Aginode reference: N521.600

LANmark-0F ZD box 12 Snap-In White

Aginode reference: N521.630

### Ruggedised and lockable Zone Distribution box

Designed for use as consolidation points, zone distribution boxes significantly increase the flexibility of desk locations in open office environments and provide a perfect solution for cabling to automation islands in an industrial setting.

The ZD boxes shall be easy to install on walls, under raised floors or in ceiling voids, due to their multiple mounting features.

They are compatible with all Snap-In copper connectors and fibre adaptors, which can be easily inserted with a simple "one-click" movement.

Optional coloured shutters need to be available to easily indicate different services when required.

This Ruggedised ZD Box shall have a lockable hinged lid for access to the Snap-In ports and a cover fastened with tamper-resistant screws for the "cabling" area.

All apertures are closed with foam strips to minimise the entry of dust into the box.

The cabling area contains all the necessary features to accommodate copper and fibre pre-term, direct terminated fibre, fibre splicing and on-site terminated copper.

The Ruggedised ZD box is also designed to facilitate installations using extractable fibre bundles and allows the breakout of bundles for splicing whilst allowing unobstructed side to side routes for the ongoing fibre.

Fibre management spiders and splice cassettes optional accessories shall be available.

A specially designed steel mounting foot (N521.6121) is available as a separate order item which raises the box 50mm from the floor slab to provide protection against water ingress.

#### Detailed product information

Example of product

LANmark Ruggedised Lockable ZD Box White

Aginode reference: N521.612

LANmark Ruggedised Lockable ZD Box Foot White

Aginode reference: N521.6121

## Plug/jack pre-terminated assemblies (CP links)

CP links are required to connect the consolidation point (CP) to the Terminal Outlet (TO)

Factory Pre-terminated  Plug/jack assemblies shall be installed to ensure a repeatable and stable level of performance.

Pre-Term Units also help reducing the installation time since connectors termination is simply eliminated.

A numbering shall be present on each leg (on both sides).

The units shall be available on order in any length from 5m up to 90m.

The 4 pair cables of the pre-terminated assemblies shall be Category 6A U/FTP to meet the quality and performance criteria necessary to ensure correct operation of the installation for frequencies up to 500 MHz and to ensure the compliance with the warranty.

The cable shall be a 4 twisted pair cable with AWG 26 stranded copper conductors and shall have an external sheathing in a material that does not give off toxic fumes (Zero Halogen) in case of fire and offer flame propagation retardant properties the cable shall be compliant to the IEC 60332-1 standard.

All four pairs shall be individually screened with an aluminium foil.

In order to provide alien cross-talk (AXT) immunity for 10 GBASE-T Ethernet transmission, the use of screened cable is mandatory.

When used in combination with horizontal cable and patch cords of the same category the full four-connector links and channels shall be guaranteed.

Factory tests in paper or electronic format shall be available on request

#### Detailed product information

Example of product

LANmark-6A Pre-Term Cat 6A U/FTP Stranded LSZH Orange Screened Jack-Plug Cat 6A unit

Aginode reference: N61A.4F11A6XC6Xnnn (nnn = length in dm)

## Optical fibre CP links

For the FTTO horizontal links OF CP links are required to connect the consolidation point (CP) to the Terminal Outlet (TO).

The use of a  robust patch cord is required for this application as the cord is going to be exposed to mechanical stress.

In order to ruggedise the patch cord each tight buffered fibre of the patch cord shall be protected by a coiled metal spring wire.

Between the spring and the LSZH jacket aramid yarns are introduced to enhance the pulling force.

| Mechanical characteristics |  |
| --- | --- |
| Crush resistance (IEC 60794-1-E3) | 500N/cm |
| Maximum pulling force (IEC 60794-1-2-E1) | 400N |
| Usage characteristics |  |
| Minimum static operating bending radius | 30mm |

The spring is very flexible and this results in a patch cord with a bend radius of only 30mm.

The patch cord has a duplex cable construction with a diameter of 2 X 2.8 mm.

It is terminated with LC connectors having a short boot of 19mm to facilitate the connection to the TO.

The Ruggedised LC patch cord is designed for indoor use and complies to following fire performance standards: IEC 60332-1 and IEC 60332-3.

Characteristics

- Patch cord cable is according to IEC 60794-2-50

- Maximum insertion loss according to IEC 61300-3-4: 0.25 dB

- Typical insertion loss: 0.15 dB

- Minimum return loss according to IEC 61300-3-6: 30 dB for MM and 50 dB for SM

- Colour of Jacket: Aqua for Multimode (OM3 and OM4) and Yellow for SM (OS2)

OF patch cords shall be designed according to the "Cross-Over" wiring principle to improve field installation (A1-B2, B1-A2). This conforms to the requirements of IEC 11801: Ed.3 and EN 50174-1 Ed.3.

#### Detailed product information

Example of product

LANmark-OF Ruggedised Patch Cord Duplex LC Duplex LC OM3 LSZH Xm Aqua

Aginode reference: N123R.5LLAX

LANmark-OF Ruggedised Patch Cord Duplex LC Duplex LC OM4 LSZH Xm Aqua

Aginode reference: N123R.7LLAX

LANmark-OF Ruggedised Patch Cord Duplex LC Duplex LC OS2 LSZH Xm Yellow

Aginode reference: N123R.4LLYX

## 24 port modular copper Patch Panels

### Flat and fixed (non sliding) patch panel

Patch panels must have 19" equipment practice dimensions to permit mounting in standard cabinets, racks or bays.

The vendor shall make their proposals for this tender using unloaded black or white 24 port Snap-In format (Modular) patch panels fitted with black or white shutters to protect the RJ45 Ports.

Optional coloured shutters need to be available to easily indicate different services when required.

The fixed Panels features a screen printed numbering systems for labelling.

If baluns, circuit cross over or impedance matchers are used, these shall be external to the Patch Panel.

The Snap-In panels feature an exclusive Clip-On system to secure the connector in the panel and to provide a simple means of bonding shielded connectors to facilitate installation. Connection of the panel to earth is achieved with a unique Auto-Connect feature removing the need for individual bonding conductors.

The installer must avoid any risk of cable pinching or compression during the installation or termination of the cables. Therefore the use of Velcro cable ties is preferred.

In the rack, the Patch Panels shall be separated by metallic patch-guides that have a closed front to protect the patch cords. The height of these guides will be 1U or 2U depending on the layout of the rack.

The Patch Panel shall also provide an automatic contact with the metal frame of the cabinet in order to ensure correct protective and functional bonding of the cabling system.

The dimensions of the patch panel shall be 19" 1 U high, depth 75 mm.

#### Detailed product information

This panel features vertical "T" clips for rapid cable retention which allows loading of the panel in around 25% of the time needed to fasten tie wraps which leads to time saving during installation.

Example of product

Patch Panel 24 Snap-In Fixed White

Aginode reference: N521.661

Example of product

Patch Panel 24 Snap-In Fixed Black

Aginode reference: N521.661BK

### Flat and sliding patch panel

Patch panels must have 19" equipment practice dimensions to permit mounting in standard cabinets, racks or bays.

The vendor shall make their proposals for this tender using unloaded black or white sliding 24 port Snap-In format (Modular) patch panels fitted with black or white shutters to protect the RJ45 Ports.

Optional coloured shutters need to be available to easily indicate different services when required.

The presentation of the Patch Panel with sliding mechanism shall provide for labelling using a printed numbering system.

If baluns, circuit cross over or impedance matchers are used, these shall be external to the Patch Panel.

The Snap-In panels feature an exclusive Clip-On system to secure the connector in the panel and to provide a simple means of bonding shielded connectors to facilitate installation. Connection of the panel to earth is achieved with a unique Auto-Connect feature removing the need for individual bonding conductors.

The installer must avoid any risk of cable pinching or compression during the installation or termination of the cables. Therefore the use of Velcro cable ties is preferred.

In the rack, the Patch Panels shall be separated by metallic patch-guides that have a closed front to protect the patch cords. The height of these guides will be 1U or 2U depending on the layout of the rack.

The Patch Panel shall also provide an automatic contact with the metal frame of the cabinet in order to ensure correct protective and functional bonding of the cabling system.

The Patch Panel with sliding mechanism has to be mounted in the cabinet before termination of the cables.

The installer shall locate the cables in the cabinet with enough slack to enable the termination of the connectors to be completed from the front of the cabinet.

The dimensions of the patch panel shall be 19" 1 U high, depth 125mm.

#### Detailed product information

This panel features vertical "T" clips for rapid cable retention which allows loading of the panel in around 25% of the time needed to fasten tie wraps which leads to time saving during installation.

Example of product

Patch Panel 24 Snap-In Sliding White

Aginode reference: N521.663

Example of product

Patch Panel 24 Snap-In sliding Black

Aginode reference: N521.663BK

### Angled copper patch panels

Patch panels must have 19" equipment practice dimensions to permit mounting in standard cabinets, racks or bays.

The vendor shall make their proposals for this tender using unloaded black or white 24 port angled Snap-In format (Modular) patch panels.

Optional coloured shutters need to be available to easily indicate different services when required.

Manufactured from steel, the panel provides a robust, high density mounting mechanism for Snap-In modular connectors and incorporates an integral cable management tray for the secure strain relief  of terminated cables.

The angled panel is designed for use in high density applications such as in Data Centres where the specially shaped panel encourages enhanced patch cord management with a reduced requirement for horizontal management bars.

The Angled Panel is recommended for use in patching frames which incorporate enhanced vertical (side) management features.

The panel features a screen printed numbering systems for labelling.

The dimensions of the patch panel shall be 19" 1 U high, depth 185 mm.

#### Detailed product information

Example of product

LANsense Panel 24 Snap-In black

Aginode reference: N521.671

LANsense Panel 24 Snap-In white

Aginode reference: N521.675

### Flat copper patch panel with Angled connectors

Patch panels must have 19" equipment practice dimensions to permit mounting in standard cabinets, racks or bays.

The Panel with angled connectors shall be a shielded 19”/1U patch panel with a fixed tray for up to 24 regular Snap-In connectors, which are mounted in an angled position inside the panel.

Six Dual Port Packs are mounted on each side, so that 12 connectors pointing to the left side and 12 connectors pointing to the right side.

Due to the angled design of the Dual Port Packs, it is possible to patch without any cable management panel above or below the panel.

Snap-In connectors can be easily fitted into the patch panel by using blue Keystone Clips, which are delivered with the panel.  The packaging of the panel does not contain connectors but is including 24 Keystone Clips for Snap-In connectors.

The panel shall be available with and without cable support tray.

The patch panels are designed for standard 19" enclosures, are 1U high, and support the following common features:

- Front colour black, similar to RAL 9005

- Designed for screened and unscreened Snap-In connectors

- Compatible with all performance categories of connector

- 24 Ports available; port numbering from left to right

- Robust steel construction

- UL94V-0

#### Detailed product information

Example of product

LANmark Patch Panel 24 Angled Snap-In Black Cable Support

Aginode reference: N521.681BK

### High density 48-port copper patch panel

Patch panels must have 19" equipment practice dimensions to permit mounting in standard cabinets, racks or bays.

The High Density Copper Patch Panel shall supports 48 Connection Points on only 1 Rack Height Unit and allows to connect full 48 port switches. It helps to reduce the space required for cabling and to free up this space to other services.

The Panel is designed to accommodate 48 Category 6A RJ45 Connectors. The Connectors are delivered together with the Panel as a Kit. The connectors come in ECO-24 packaging for bulk termination.

It is a robust, fully metal Patch Panel, which supports the weight load of 48 cables and offers a rear cable management with 48 T-connection points for Tie-Wraps.

Connectors are mounted Latch Up / Latch Down to enable easy patching of RJ45 Cords. Port Numbering is on the opposite side of the latch to keep it visible. Numbering is horizontal from left to right.

Connection of the panel to earth is achieved with a unique Auto-Connect feature removing the need for individual bonding conductors or earthing screws at the rear of the panel.

#### Detailed product information

Example of product

LANmark Patch Panel 48 EVO 1U Black Kit with 48 Cat 6A Connectors

Aginode reference: N521.668KIT

## Copper Patch cords

Here below select the right Class/category (E & 6 / EA & 6A / F & 7 or FA & 7A) and delete other ones.

To achieve a Class E/EA/FA Channel performance all data Patch Cords shall be Category 6/6A/7A rated.

The patch cord cable shall be made from LSZH material with a print legend indicating type of cable, brand name, production code and metre mark.

All patch cords shall be compliant to the IEC 60332-1 standard to offer flame propagation retardant properties.

### Cat.6 unscreened patch cords

All Data patch cords shall be unscreened.

The standard colours offered for the LSZH flame retardant jacket shall be orange and dark grey.

Red, Blue, Green and Yellow colours shall also be available on demand.

The default lengths available from stock shall be 1, 2, 3, 5, 10 and 20m. in order to ensure quick delivery of the cords on site. Other lengths shall be available on demand.

The patch cords feature a slim over-moulded boot which is kept inside the RJ45 boundaries to enable High Density Patching with 48 cords in 1 height unit.

They also come with a ‘Replaceable’ black Latch Protector, which can be used for colour coding of different services.

The coloured retrofit latch protectors shall be available as accessory in 8 colours for colour coding of different services.

The cords shall be fitted with Category 6 RJ45 plugs, with a Self-latching connector. All pairs must have an impedance of 100 Ohms. The characteristic impedance of the pairs must be identical to that of the horizontal cables. The Patch Cords shall have a guaranteed performance level of greater than 750 insertions without degradation to the performance level of the solution.

The cable used for the Patch Cords shall be Category 6 LSZH unscreened patch cable. The cable shall be a 4 twisted pair cable with stranded conductors. Traceability numbers should accompany the cables supplied from the manufacturers packaging to assist in quality validation of the installed cable.

When used with the LANmark-6 system, Cat 6/Class E channel performance complies with the channel limits of TIA/EIA-568-C2 and ISO/IEC 11801: 2017 and it exceeds the requirements of the ISO/IEC 4-connector model.

#### Detailed product information

Example of products

### Cat.6 unscreened small diameter patch cords

Cat.6 Slimflex UniBoot cords are designed to offer a reduced sized patching solution, whilst fully supporting Gigabit Ethernet or any other Category 6 / Class E application.

The cable is built with AWG28 stranded copper conductors and has an overall diameter of only 4 mm, as opposed to traditional Category 6 cords which have a typical width of around 6 mm.

As a result, Slimflex cords can reduce bundle sizes with 53% compared with traditional cordage. This is particularly useful in high density patching areas in telecommunications rooms, where space-saving and ease of cord management are crucial.

The patch cords feature a slim over-moulded boot which is kept inside the RJ45 boundaries to enable High Density Patching with 48 cords in 1 height unit.

They also come with a ‘Replaceable’ black Latch Protector, which can be used for colour coding of different services.

The coloured retrofit latch protectors shall be available as accessory in 8 colours for colour coding of different services.

The cords shall be fitted with Category 6 RJ45 plugs, with a Self-latching connector. All pairs must have an impedance of 100 Ohms. The characteristic impedance of the pairs must be identical to that of the horizontal cables. The Patch Cords shall have a guaranteed performance level of greater than 750 insertions without degradation to the performance level of the solution.

The cable used for the Patch Cords shall be Category 6 LSZH unscreened patch cable. The cable shall be a 4 twisted pair cable with stranded conductors. Traceability numbers should accompany the cables supplied from the manufacturers packaging to assist in quality validation of the installed cable.

When used with the LANmark-6 system, Cat 6/Class E channel performance complies with the channel limits of TIA/EIA-568-C2 and ISO/IEC 11801: 2017 and it exceeds the requirements of the ISO/IEC 4-connector model.

#### Detailed product information

Example of products

### Cat.6 screened patch cords

All Data patch cords shall be fully screened.

The standard colours offered for the LSZH flame retardant jacket shall be orange and dark grey.

Red, Blue, Green and Yellow colours shall also be available on demand.

The default lengths available from stock shall be 1, 2, 3, 5, 10 and 20m. in order to ensure quick delivery of the cords on site. Other lengths shall be available on demand.

The patch cords feature a slim over-moulded boot which is kept inside the RJ45 boundaries to enable High Density Patching with 48 cords in 1 height unit.

They also come with a ‘Replaceable’ black Latch Protector, which can be used for colour coding of different services.

The coloured retrofit latch protectors shall be available as accessory in 8 colours for colour coding of different services.

The cords shall be fitted with Category 6 RJ45 screened plugs, with a Self-latching connector. All pairs must have an impedance of 100 Ohms. The characteristic impedance of the pairs must be identical to that of the horizontal cables. The Patch Cords shall have a guaranteed performance level of greater than 750 insertions without degradation to the performance level of the solution.

The cable used for the Patch Cords shall be Category 6 LSZH screened patch cable. The cable shall be a 4 twisted pair cable with stranded conductors. Traceability numbers should accompany the cables supplied from the manufacturers packaging to assist in quality validation of the installed cable.

When used with the LANmark-6 system, Cat 6/Class E channel performance complies with the channel limits of TIA/EIA-568-C2 and ISO/IEC 11801: 2017 and it exceeds the requirements of the ISO/IEC 4-connector model.

#### Detailed product information

Example of products

### Cat.6A screened data patch cords

All Data patch cords shall be fully screened.

The standard colours offered for the LSZH flame retardant jacket shall be orange and dark grey.

Red, Blue, Green and Yellow colours shall also be available on demand.

The default lengths available from stock shall be 1, 2, 3, 5, 10 and 20m. in order to ensure quick delivery of the cords on site. Other lengths shall be available on demand.

The patch cords feature a slim over-moulded boot which is kept inside the RJ45 boundaries to enable High Density Patching with 48 cords in 1 height unit.

They also come with a ‘Replaceable’ black Latch Protector, which can be used for colour coding of different services.

The coloured retrofit latch protectors shall be available as accessory in 8 colours for colour coding of different services.

The cords shall be fitted with Category 6A RJ45 screened plugs, with a Self-latching connector. All pairs must have an impedance of 100 Ohms. The characteristic impedance of the pairs must be identical to that of the horizontal cables. The Patch Cords shall have a guaranteed performance level of greater than 750 insertions without degradation to the performance level of the solution.

The cable used for the Patch Cords shall be Category 6A LSZH U/FTP patch cable. The cable shall be a 4 twisted pair cable with individually screened stranded conductors. Traceability numbers should accompany the cables supplied from the manufacturers packaging to assist in quality validation of the installed cable.

When used with the LANmark-6A system, Cat 6A/Class EA channel performance complies with the channel limits of TIA/EIA-568-C2 and ISO/IEC 11801: 2017and it exceeds the requirements of the ISO/IEC 4-connector model.

#### Detailed product information

Example of products

### Cat.6A screened small diameter patch cords

Cat. 6A Slimflex cords are developed to support 10 Gigabit Ethernet (IEEE 802.3an) and any other Cat.6A application and require 44 % less space than regular Cat6A patch cords.

They use thin AWG30 wires inside a cable with an outer diameter of only 4.5mm. When formed into bundles, this results into significant space savings.

LANmark-6A Slimflex Cords offer a frequency range up to 500MHz and are matched with other LANmark-6A components to provide improved data throughput in complex channel configurations. They use stranded cable to provide maximum flexibility.

The patch cords feature a slim over-moulded boot which is kept inside the RJ45 boundaries to enable High Density Patching with 48 cords in 1 height unit.

They also come with a ‘Replaceable’ black Latch Protector, which can be used for colour coding of different services.

The coloured retrofit latch protectors shall be available as accessory in 8 colours for colour coding of different services.

The cords shall be fitted with Category 6A RJ45 screened plugs, with a Self-latching connector. All pairs must have an impedance of 100 Ohms. The characteristic impedance of the pairs must be identical to that of the horizontal cables. The Patch Cords shall have a guaranteed performance level of greater than 750 insertions without degradation to the performance level of the solution.

The cable used for the Patch Cords shall be Category 6A LSZH screened patch cable. The cable shall be a 4 twisted pair cable with stranded conductors. Traceability numbers should accompany the cables supplied from the manufacturers packaging to assist in quality validation of the installed cable.

The LANmark-6A Slimflex cords fully comply and exceed the requirements of ISO11801:2017, except the maximum length requirements. The maximum length of channels is reduced to 96m. The cord derating factor is 2.6.
Used with other Cat. 6A components of the same manufacturer, very short Cat 6A link and channel configurations with up to 3 connection points within 10 meters can be supported.

#### Detailed product information

Example of products

### Cat.7A screened data patch cord

All Cat.7A Data patch cords shall be full screened. The standard colour offered for the LSZH flame retardant jacket shall be orange.

The cords shall be fitted with Category 7A GG45 plugs, booted at each connector.

The Cat.7A plugs shall be compliant to the IEC 61076-3-110 standard.

The characteristic impedance of the pairs must be identical to that of the horizontal cables. The Patch Cords shall have a guaranteed performance level of greater than 750 insertions without degradation to the performance level of the solution.

The cable used for the Patch Cords shall be Category 7A S/FTP patch cable. The cable shall be a 4 twisted pair cable with stranded conductors. Traceability numbers should accompany the cables supplied from the manufacturers packaging to assist in quality validation of the installed cable.

All pairs must have an impedance of 100 Ohms.

When used with the LANmark-7A system, Cat 7A/Class FA channel performance complies with the channel limits of TIA/EIA-568-C2 and ISO/IEC 11801: 2017 and it exceeds the requirements of the ISO/IEC 4-connector model.

#### Detailed product information

Example of products

### Cat.6A Secure Lock RJ45 Patch cords

Security being of paramount importance for the current project the copper sub-system shall be equipped with a system restricting the removal of the RJ45 patch cords.

The range of Secure Lock patch cords shall be designed to meet the needs of applications such as:

- PoE connector protection (damage caused by mating/unmating under load)

- Theft prevention (Hotels/Schools/Libraries)

- Critical circuit protection

- Patch Cord availability (Meeting rooms)

- Redundant Copper links

- Connection of IP security cameras

- Use in high-density switches.

There are two variants in the LANmark-6A Secure Lock Patch Cords:

- Patch Cords with locks on both the plugs

- Patch Cords with lock on only one plug

Each cord comes preassembled with a red locking boot.

The cord can be disconnected when the matching red key is used to unlock the boot.

The standard cord colour of the LSZH jacket shall be orange.

Standard cords (cat.6A S/FTP) are stocked in lengths of 1, 2, 3 and 5m - other lengths are available on demand.

#### Detailed product information

Example of products

Example of products

LANmark Secure Lock Copper Patch Cord Key

Aginode reference: N1LA.KEY

### Secure Lock RJ45 port blockers

Port Blockers shall secure the network infrastructure by blocking out unused or unauthorised ports.

They also protect the hardware from incoming dust and harmful foreign objects.

RJ45 Port Blockers shall fit into any standard RJ45 jack without the use of a tool.

The insertion shall be tool-free onto any standard RJ45 Jack used for outlets and Patch Panels

A dedicated black coloured key must be needed to unlock and remove Port Blockers.

Features

- Exchangeable and re-usable

- Individual packaging for Secure Lock RJ45 Port blockers should contain 100pcs

- Individual packaging for Secure Lock RJ45 Port Key should contain 5pcs

- Material: Plastic

- UL Rating: UL94V-2

- RoHS 2 compliant

- Colour of the RJ45 Port Blocker: Red, Blue and Black

- Colour of the RJ45 Port Key: Black

- Operating temperature range: -10°C~60°C

- Storage temperature range: -40°C~60°C

- Humidity: 10%~90%RH

#### Detailed product information

Example of products

LANmark Secure Lock RJ45 Port Blocker – Blue

Aginode reference: N110.SRJPBB

LANmark Secure Lock RJ45 Port Blocker – Red

Aginode reference: N110.SRJPBR

LANmark Secure Lock RJ45 Port Blockers – Black

Aginode reference: N110.SRJPBK

LANmark Secure Lock RJ45 Port Blocker Key

Aginode reference: N110.SRJPKK

## Link and Channel performance

### Cat.6 performance

Manufacturer shall demonstrate guaranteed minimum worst-case (4-connector Link) performance to be compliant with class E link and channel performance according to the ISO/IEC 11801: 2017 standard.

Components used must be compliant with the Category 6 standard mentioned above.

The performance of both the components and the link and channel should show stable performance up to 250MHz in order to allow for possible future applications requiring crosstalk cancellation up to 250MHz.

The system supplier must be able to demonstrate in house design and manufacturing expertise for all components used (e.g. cables, outlets, panels and cords) in order to ensure compatibility of system elements.

### Cat.6A performance

Manufacturer shall demonstrate guaranteed minimum worst-case (4-connector Link) performance to be compliant with class EA link and channel performance according to the ISO/IEC 11801: 2017 ed.3 standard.

The system supplier must be able to demonstrate in house design and manufacturing expertise for all components used (e.g. cables, outlets, panels and cords) in order to ensure compatibility of system elements.

Regarding short links, the standard channel performance shall be warranted for a 10 meters / 3 connectors link with 5 meters of cable length for both Patch Panel to Consolidation Point and Consolidation Point to Terminal Outlet segments.

The Cat.6A channel shall comply to the following electrical performances.

Maximum and Minimum values shall be warranted by the manufacturer.

All values are based on Worst Case 4 Connector Channel configurations according to ISO11801:2011.

Standard (Std) values are based on ISO11801:2017 Class EA.

Minimal and maximum values represent guaranteed channel performance.

### Cat.7A performance

Components used must be compliant with both the Category 6A and Category 7A standards mentioned above.

The performance of both the components and the link should show stable performance up to 1,000MHz in order to allow for possible future applications.

The performance of the channel should show stable performance

- Up to 500MHz when using Cat.6A patch cords

- Up to 1,250MHz when using Cat.7A patch cords

The system supplier must be able to demonstrate in house design and manufacturing expertise for all components used (e.g. cables, outlets, panels and cords) in order to ensure compatibility of system elements.

All components shall be produced by the same system manufacturer.

Electrical Performance Class FA 4 Connectors Channels:

# Intra-Building Backbone Cabling

This backbone will link the Switches located in the Floor Distributors (FD) to the Data Centre switches  through the Building Distributor (BD).

## Optical Fibre

### OM3 fibre characteristics

The multi-core optical fibre cable shall consist of multimode OM3 - 50/125µ fibre with fibres colour coding for identification.

The OM3 fibres shall be compliant to the following standards:

- EC 60793-1-49: differential mode delay (DMD) to measure effective modal bandwidth (EMB)

- EC 60793-1-41: overfilled mode launch bandwidth (OFL BW)

- ISO/IEC 11801: 2017 ed.3 as OM3 fibre

- IEC 60793-2-10 as fibre type A1a.2b

- Compliant to annex D2 (DMD template requirements) and annex D3 (EMBc: calculated effective modal bandwidth) of IEC 60793-2-10 ed. 4.

The OM3 fibres shall meet the following specifications:

Geometrical Characteristics of OM3 fibres

| Characteristics | Spec. Values | Unit |
| --- | --- | --- |
| Core Diameter | 50 ± 2.5 | µm |
| Core Non-Circularity | ≤ 6.0 | % |
| Core/Clad Concentricity | ≤ 1.5 | µm |
| Cladding Diameter | 125 ± 1.0 | µm |
| Cladding Non-Circularity | ≤ 1.0 | % |
| Coating Diameter | 250 ± 15.0 | µm |
| Coating/Clad Concentricity Error | ≤ 10.0 | µm |

Optical parameters of OM3 fibres

Effective modal bandwidth shall be measured according to the templates method of IEC 60793-2-10 section D2 and the calculated effective modal bandwidth of IEC 60793-2-10 section D3.

| Characteristics | Spec Values | Unit |
| --- | --- | --- |
| Bandwidth (Overfilled Launch) 850 nm | ≥ 1500 | Mhz.km |
| Bandwidth (Overfilled Launch) 1300 nm | ≥ 500 | Mhz.km |
| Effective Modal Bandwidth (EMB) 850 nm | ≥ 2000 | Mhz.km |
| Transmission link lengths for 1 Gb/s (SX/LX) | 880/550 | m |
| Transmission link lengths for 10 Gb/s (SR/LX4) | 330/300 | m |
| Transmission link lengths for 40 Gb/s (SR4) | 100 | m |
| Transmission link lengths for 100 Gb/s (SR4) | 70 | m |
| Attenuation 850 nm | 3.0 | dB/km |
| Attenuation 1300 nm | 1.0 | dB/km |
| Attenuation uniformity | ≤ 0.2 | dB |
| Numerical Aperture | 0.20 ± 0.02 |  |

### OM4 fibre characteristics

The multi-core optical fibre cable shall consist of multimode OM4 - 50/125µ fibre with fibres colour coding for identification.

The OM4 fibres shall be compliant to the following standards:

- EC 60793-1-49: differential mode delay (DMD) to measure effective modal bandwidth (EMB)

- EC 60793-1-41: overfilled mode launch bandwidth (OFL BW)

- ISO/IEC 11801: 2017 ed.3 as OM4 fibre

- IEC 60793-2-10 as fibre type A1a.3b

The OM4 fibres shall meet the following specifications:

Geometrical Characteristics of OM4 fibres

| Characteristics | Spec. Values | Unit |
| --- | --- | --- |
| Core Diameter | 50 ± 2.5 | µm |
| Core Non-Circularity | ≤ 6.0 | % |
| Core/Clad Concentricity | ≤ 1.5 | µm |
| Cladding Diameter | 125 ± 1.0 | µm |
| Cladding Non-Circularity | ≤ 1.0 | % |
| Coating Diameter | 250 ± 15.0 | µm |
| Coating/Clad Concentricity Error | ≤ 10.0 | µm |

Optical parameters of OM4 fibres

Effective modal bandwidth shall be measured according to the templates method of IEC 60793-2-10 section D4 and the calculated effective modal bandwidth of IEC 60793-2-10 section D5.

| Characteristics | Spec Values | Unit |
| --- | --- | --- |
| Bandwidth (Overfilled Launch) 850 nm | ≥ 3500 | Mhz.km |
| Bandwidth (Overfilled Launch) 1300 nm | ≥ 500 | Mhz.km |
| Effective Modal Bandwidth (EMB) 850 nm | ≥ 4700 | Mhz.km |
| Transmission link lengths for 1 Gb/s (SX/LX) | 900/550 | m |
| Transmission link lengths for 10 Gb/s (SR/LX4) | 550*/300 | m |
| Transmission link lengths for 40 Gb/s (SR4) | 150* | m |
| Transmission link lengths for 100 Gb/s (SR4) | 100 | m |
| Attenuation 850 nm | 3.0 | dB/km |
| Attenuation 1300 nm | 1.0 | dB/km |
| Attenuation uniformity | ≤ 0.2 | dB |
| Numerical Aperture | 0.20 ± 0.02 |  |
| * with engineered link of maximum 1.0 dB connector insertion loss |  |  |

### OM5 fibre characteristics

The multi-core optical fibre cable shall consist of multimode OM5 - 50/125µ fibre with fibres colour coding for identification.

The OM5 fibres shall be compliant to the following standards:

- EC 60793-1-49: differential mode delay (DMD) to measure effective modal bandwidth (EMB)

- EC 60793-1-41: overfilled mode launch bandwidth (OFL BW)

- ISO/IEC 11801: 2017 ed.3 as OM5 fibre

- IEC 60793-2-10 as fibre type A1a.4b

The OM5 fibres shall meet the following specifications:

Geometrical Characteristics of OM5 fibres

| Characteristics | Spec. Values | Unit |
| --- | --- | --- |
| Core Diameter | 50 ± 2.5 | µm |
| Core Non-Circularity | ≤ 6.0 | % |
| Core/Clad Concentricity | ≤ 1.5 | µm |
| Cladding Diameter | 125 ± 1.0 | µm |
| Cladding Non-Circularity | ≤ 1.0 | % |
| Coating Diameter | 250 ± 15.0 | µm |
| Coating/Clad Concentricity Error | ≤ 10.0 | µm |

Optical parameters of OM5 fibres

Effective modal bandwidth shall be measured according to the templates method of IEC 60793-2-10 section D4 and the calculated effective modal bandwidth of IEC 60793-2-10 section D5.

* with engineered link of maximum 1.0 dB connector insertion loss

### OS2 fibre characteristics

The multi-core optical fibre cable shall consist of singlemode OS2 - 9/125µ fibre with fibres colour coding for identification.

The OS2 fibres shall be compliant to the following standards:

- ITU-T as fibre type G.657.A1

- Singlemode OS2 cable defined in ISO/IEC 11801 - 3rd edition

- IEC 60793-1

- IEC 60793-2-50 as fibre type B6.a1

The OS2 fibres shall meet the following specifications:

Macrobend loss

Optical parameters of OS2 fibres

## Fibre pre-terminated cable assembly

### UHD LC fibre pre-terminated cable assembly

The Ultra High Density (UHD) assembly consists of a Micro-Bundle Indoor cable terminated with connectors on each side in a factory.

Cable structure

Every fibre shall be 250µm diameter secondary coated each being a different colour or suitably identified for termination identification.

The cable shall be a Micro-Bundle construction, limited  filled with gel, containing 12 fibres, with a maximum of 8 Micro-Bundles around the central strength element. The Micro-Bundles are protected with reinforced glass yarns. The jacket material shall be LSZH.

The cable central strength element shall be glass yarn. The cable shall be dielectric construction, i.e. with no metallic content.

The cable shall be flame and fire retardant according to IEC 60332-1 and IEC 60332-3.

The cable shall be compliant to the IEC 60794-2-20 standard.

The Pre-Term shall have a dual stage fan-out design.

The first fan-out stage is the transition point between the cable and the legs of the fan-out. Each leg of the fan-out contains 1 Micro-Bundle with 12 fibres inside. This fan-out has been reinforced with aramid yarns.

The second fan-out stage distributes the reinforced Micro-Bundle into 12 buffered fibres. The second fan-out together with the 12 buffered fibres and connectors are optimized for installation and fixation into the UHD adaptor modules.

The connectors on the Tight Buffered fibres have coloured boots for identification in compliance with the TIA/EIA standard. In manufacturing a fibre pair flip has been implemented.  When installing the connectors inside the modules of the patch panel the coloured boots need to match the colours of the integrated strip inside the module to obtain transmit-receive polarity in the channel.

The fan-out is protected with a bubble foam for protection during transport and installation. In addition every bundle of 12 connectors has an additional individual protection to avoid mixing them up with connectors from another bundle.

The Pre-Terms are optimized for both laying and pulling. A pulling eye system is positioned at one side of the Pre-Term to facilitate the installation. This pulling eye is connected to the internal strength element of the cable. The maximum pulling force on the pulling eye is 450N.

The LC/LC Pre-Terms come with a PG-13 cable gland that fits into the patch panel slots.

In order to reduce overlengths in data centres the Pre-Terms are custom made and available with 1m increments.

The typical value for the insertion loss for the low loss LC/LC connection is 0,15 dB. The limit value is 0,25 dB measured according to standard IEC61300-3-4. The minimum return loss is measured according to standard IEC 61300-3-6.  For a multimode LC connection the RL is 30 dB, for a singlemode LC connection it is 40 dB and for a LC/APC connection it is 55 dB.

All LANmark-OF Pre-term assemblies are fully terminated and tested in a quality assured factory environment. The test results are delivered in the box with the Pre-Term.

Performances

The following performances shall be warranted by the manufacturer:

#### CPR grade compliance requirement (Cca s1,d0,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1,d0,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information

Example of product

LANmark-OF ENSPACE LC/LC Pre-Term

Aginode references

## OF cable

### Tight Buffered Universal OF cable

This optical fibre cable shall be used for indoor home run back to patch panel routes in risers, horizontal applications and for outdoor duct applications where ducts can be temporarily flooded. This cable shall be selected where the required fibre count is from 4 to 24.

The cable shall be suitable for connector manufacturer field termination processes (SC or LC connectors) and for OF pigtails splicing.

The cable shall be a dry construction i.e. with no gel content. The jacket material shall be waterproof and rodent retardant LSZH.

The cable shall be flame and fire retardant according to IEC 60332-1 and IEC 60332-3.

Every fibre shall be 900µm diameter secondary coated each being a different colour or suitably identified for termination identification. Allow 10 cm stripping of the tight buffer in one action.

The cable strength member shall be water tight glass yarn laid longitudinally between the fibres and the inside wall of the LSZH UV resistant outer jacket. A central strength element is the core of the cable and used to pulling cables in a duct.

The cable shall be dielectric construction, i.e. with no metallic content.

The cable shall be compliant to the IEC 60794-2-21 standard.

Construction characteristics

Fibre optic type OM3 50/125, OM4 50/125 or OS2 9/125

#### CPR grade compliance requirement (Cca s1,d1,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1,d1,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1,d1,a1)

Example of product

LANmark-OF Tight Buffer Universal 12x Multimode 50/125 OM3 LSZH Cca S1 d1 a1 Aqua

Aginode reference: N165.TBUN12-AC

LANmark-OF Tight Buffer Universal 24x Multimode 50/125 OM3 LSZH Cca S1 d1 a1 Aqua

Aginode reference: N165.TBUN24-AC

LANmark-OF Tight Buffer Universal 12x Multimode 50/125 OM4 LSZH Cca S1 d1 a1 Aqua

Aginode reference: N167.TBUN12-AC

LANmark-OF Tight Buffer Universal 24x Multimode 50/125 OM4 LSZH Cca S1 d1 a1 Aqua

Aginode reference: N167.TBUN24-AC

LANmark-OF Tight Buffer Universal 12x Singlemode 9/125 OS2 LSZH Cca S1 d1 a1 Yellow

Aginode reference: N164.TBUN12-YC

LANmark-OF Tight Buffer Universal 24x Singlemode 9/125 OS2 LSZH Cca S1 d1 a1 Yellow

Aginode reference: N164.TBUN24-YC

### Micro-Bundle Universal OF cable (4F – 12F)

This optical fibre cable shall be used for indoor home run back to patch panel routes in risers, horizontal applications and for outdoor duct applications where ducts can be temporarily flooded.

Every fibre shall be 250µm diameter secondary coated each being a different colour or suitably identified for termination identification.

The cable shall be a micro-Bundle construction, limited filled with gel, containing 12 fibres, with a maximum of 6 micro-Bundles around the central strength element. Since there is no drip effect of the very limited amount of gel the cable shall be optimised for both horizontal and vertical installations.

The jacket material shall be waterproof LSZH with a UV resistant additive .The cable shall be dielectric construction, i.e. with no metallic content with reinforced watertight glass yarns and shall provide rodent resistance.

This micro-bundle cable has a capacity of 4 up to 12 fibres and is designed for splicing with pigtails.

The cable shall be flame and fire retardant according to IEC 60332-1 and IEC 60332-3.

The cable shall be compliant to the IEC 60794-2-20 standard.

Construction characteristics

Fibre optic type OM3 50/125, OM4 50/125 and OS2 9/125

#### CPR grade compliance requirement (Cca s1,d0,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1,d0,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1,d0,a1)

Example of product

LANmark-OF Micro-Bundle Universal 4x Multimode 50/125 OM3 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N165.MBUN04-AC

LANmark-OF Micro-Bundle Universal 12x Multimode 50/125 OM3 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N165.MBUN12-AC

LANmark-OF Micro-Bundle Universal 4x Multimode 50/125 OM4 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N167.MBUN04-AC

LANmark-OF Micro-Bundle Universal 12x Multimode 50/125 OM4 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N167.MBUN12-AC

LANmark-OF Micro-Bundle Universal 4x Singlemode 9/125 OS2 LSZH Cca s1 d0 a1 Yellow

Aginode reference: N164.MBUN04-YC

LANmark-OF Micro-Bundle Universal 12x Singlemode 9/125 OS2 LSZH Cca s1 d0 a1 Yellow

Aginode reference: N164.MBUN12-YC

### Micro-Bundle Universal OF cable (24F – 96F)

This optical fibre cable shall be used for indoor home run back to patch panel routes in risers, horizontal applications and for outdoor duct applications where ducts can be temporarily flooded. This cable shall be selected where the required fibre count is 24, 48 or 96.

Every fibre shall be 250µm diameter secondary coated each being a different colour or suitably identified for termination identification.

The cable shall be a micro-Bundle construction, limited filled with gel, containing 12 fibres, with a maximum of 8 micro-Bundles around the central strength element. Since there is no drip effect of the very limited amount of gel the cable is optimised for both horizontal and vertical installations.

The jacket material shall be waterproof LSZH with a UV resistant additive .The cable shall be dielectric construction, i.e. with no metallic content with reinforced watertight glass yarns and shall provide rodent resistance.

The cable shall be flame and fire retardant according to IEC 60332-1 and IEC 60332-3.

Construction characteristics

Fibre optic type OM3 50/125, OM4 50/125 or OS2 9/125

#### CPR grade compliance requirement (Cca s1,d0,a1)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Cca s1,d0,a1 and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Cca s1,d0,a1)

Example of product

LANmark-OF Micro-Bundle Universal 24x Multimode 50/125 OM3 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N165.MBUN24-AC

LANmark-OF Micro-Bundle Universal 96x Multimode 50/125 OM3 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N165.MBUN96-AC

LANmark-OF Micro-Bundle Universal 24x Multimode 50/125 OM4 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N167.MBUN24-AC

LANmark-OF Micro-Bundle Universal 96x Multimode 50/125 OM4 LSZH Cca s1 d0 a1 Aqua

Aginode reference: N167.MBUN96-AC

LANmark-OF Micro-Bundle Universal 24x Singlemode 9/125 OS2 LSZH Cca s1 d0 a1 Yellow

Aginode reference: N164.MBUN24-YC

LANmark-OF Micro-Bundle Universal 96x Singlemode 9/125 OS2 LSZH Cca s1 d0 a1 Yellow

Aginode reference: N164.MBUN96-YC

### Outdoor OF cable with dielectric armour - PE

This optical fibre cable is suitable for outdoor use in ducts and for also for direct burial.

This cable is Campus oriented.

The cable shall be suitable for OF pigtails splicing.

The cable shall be a central loose tube construction with reinforced watertight glass yarns. The jacket material shall be waterproof HDPE and UV resistant.

Every fibre shall be 250µm diameter secondary coated each being a different colour or suitably identified for termination identification.

The construction shall be a full dielectric armouring design providing rodent resistance. The dielectric armouring consists of half FRP elements and half fillers. The tube is gel filled and has a capacity of 4 up to 24 fibres.

Construction characteristics

Fibre optic type OM3 50/125, OM4 50/125 or OS2 9/125

#### Detailed product information

Example of product

LANmark-OF UD 12x Multimode 50/125 OM3 PE Black

Aginode reference: N165.UDPE12B

LANmark-OF UD 12x Multimode 50/125 OM4 PE Black

Aginode reference: N167. UDPE12B

LANmark-OF UD 12x Multimode 50/125 OS2 PE Black

Aginode reference: N164. UDPE12B

LANmark-OF UD 24x Multimode 50/125 OM3 PE Black

Aginode reference: N165. UDPE24B

LANmark-OF UD 24x Multimode 50/125 OM4 PE Black

Aginode reference: N167. UDPE24B

LANmark-OF UD 24x Singlemode 9/125 OS2 PE Black

Aginode reference: N164. UDPE24B

### Universal OF cable with metallic armour - LSZH

This optical fibre cable is suitable for indoor and outdoor use in ducts and for also for direct burial.

This cable is Campus oriented.

The cable shall be suitable for OF pigtails splicing.

The cable shall be a central loose tube construction with reinforced watertight glass yarns. The jacket material shall be waterproof LSZH and UV resistant.

Every fibre shall be 250µm diameter secondary coated each being a different colour or suitably identified for termination identification.

The armour shall consist of a corrugated steel tape armouring providing full rodent protection. The tube is gel filled and has a capacity of 4 up to 24 fibres.

The cable shall be flame and fire retardant according to IEC 60332-1 and IEC 60332-3.

Construction characteristics

Fibre optic type OM3 50/125, OM4 50/125 or OS2 9/125

| Usage characteristics |  |
| --- | --- |
| Nominal outer diameter | 8.5 mm |
| Approximate weight | 104 kg/km |
| Mechanical characteristics |  |
| Maximum pulling force (IEC 60794-1-2-E1) | 1500N |
| Maximum operating pulling force | 450N |
| Mechanical resistance to impacts | 3 impacts of 5 N.m |
| Crush resistance (IEC 60794-1-E3) | 300N/cm |
| Usage characteristics |  |
| Minimum dynamic operating bending radius | 170 mm |
| Minimum static operating bending radius | 130 mm |
| Ambient installation temperature, range | 0 .. 40°C |
| Operating temperature, range | -40 .. 60°C |
| Storage temperature, range | -40 .. 60°C |
| Fire retardant | IEC 60332-3 |
| Flame retardant | IEC 60332-1 |

#### CPR grade compliance requirement (Eca)

The CPR regulations came into force in July 2016 and with effect from the 1st July 2017, cable jacket

materials must be of the appropriate Construction Product Regulations Class to meet the

requirements of EN 50399 and EN 50575 2014/A:2016 standards. In particular the cables proposed for this project must conform with EN50575 for certification and labelling.

The proposed cables must meet Class Eca and the bidder must provide a statement from the chosen manufacturer detailing their 3rd party verification of their product and its classification.

#### Detailed product information (CPR grade Eca)

Example of product

LANmark-OF UC Universal 12x Multimode 50/125 OM3 LSZH Eca Black

Aginode reference: N165.UCUN12B

LANmark-OF UC Universal 12x Multimode 50/125 OM4 LSZH Eca Black

Aginode reference: N167.UCUN12B

LANmark-OF UC Universal 12x Singlemode 9/125 OS2 LSZH Eca Black

Aginode reference: N164.UCUN12BE

LANmark-OF UC Universal 24x Multimode 50/125 OM3 LSZH Eca Black

Aginode reference: N165.UCUN24B

LANmark-OF UC Universal 24x Multimode 50/125 OM4 LSZH Eca Black

Aginode reference: N167.UCUN24B

LANmark-OF UC Universal 24x Singlemode 9/125 OS2 LSZH Eca Black

Aginode reference: N164.UCUN24B

### Outdoor OF cable with lateral Strength Members - LSZH

This optical fibre cable is suitable for outdoor use in ducts and for also for direct burial.

This cable is Campus oriented.

The cable shall be suitable for OF pigtails splicing.

This cable shall be selected where the required fibre count is 12 or 24.

Every fibre shall be 250µm diameter secondary coated each being a different colour or suitably identified for termination identification.

The cable is designed for indoor and outdoor installation. The design is made of a central loose tube surrounded by reinforcing yarns and a LSZH jacket incorporating 2 lateral strength members.

The cable is watertight due to the gel in the loose tube and the watertight swellable yarns

.

The cable shall be flame and fire retardant according to IEC 60332-1 and IEC 60332-3.

Construction characteristics

Fibre optic type OM3 50/125, OM4 50/125 or OS2 9/125

#### Detailed product information

Example of product

LANmark-OF UGUN 12x Multimode 50/125 OM3 LSZH B2ca s1d0a1 Black

Aginode reference: N165.UGUN12-BB

LANmark-OF UGUN 12x Multimode 50/125 OM4 LSZH B2ca s1d0a1 Black

Aginode reference: N167. UGUN12-BB

LANmark-OF UGUN 12x Singlemode 50/125 OS2 LSZH B2ca s1d0a1 Black

Aginode reference: N164. UGUN12-BB

LANmark-OF UGUN 24x Multimode 50/125 OM3 LSZH B2ca s1d0a1 Black

Aginode reference: N165.UGUN24-BB

LANmark-OF UGUN 24x Multimode 50/125 OM4 LSZH B2ca s1d0a1 Black

Aginode reference: N167. UGUN24-BB

LANmark-OF UGUN 24x Singlemode 50/125 OS2 LSZH B2ca s1d0a1 Black

Aginode reference: N164. UGUN24-BB

## Optical Fibre Patch Panel

### Sliding modular OF Patch Panel

The 1U Optical Fibre Patch Panel must be modular having 2” empty ports that can be loaded with SC or LC Snap-In adaptors and  fits in a 19” rack or cabinet.

The modular OF panel has extended cable management with multiple entries to provide maximum flexibility. It accommodates both cable glands and tie wraps for strain relief of the cables. The cable gland sizes holes are 20 mm (8x) and 25 mm (2x).

The patch panel shall be designed with an enhanced sliding mechanism enabling front side installation and maintenance work to be carried out without having to remove the entire panel.

The front adaptor plate is fixed in a recessed position in the chassis of the panel. When set in recess position the front connector plate is deeper than the front of the 19" rails of the cabinet. This will provide sufficient bend radius for the patch cords once connected to the panel. This shall also prevent damages to the patch cords when the cabinet doors are closed.

Direct Termination of the connectors (SC & LC) on to the fibres as well as splicing of pigtails (SC & LC) shall be possible.

The patch panel chassis has multiple, specially designed, slots at the rear to fix the cable glands of  pre-terminated cables. There shall be ample space inside the patch panel to organise the flexible fan-out of the pre-terminated cables.

The Patch Panel shall be supplied with 3 loop rings to neatly coil the terminated fibres.

Up to four optional splice cassettes should be supported to manage up to 48 splices with heat shrink protectors and with aluminium protectors.

The splice cassettes shall feature a lifting functionality for improved ease of installation and inspection.

The front plate of the 24 port modular Patch Panel shall be compatible with the following connector types:  24 single SC, 24 duplex LC and 12 duplex DSC.

Standard LC, SC and DSC Snap-In couplers shall be available to load the modular patch panel.

The colour of the Multimode Snap-In adaptors shall be aqua.

Singlemode Snap-In adaptors shall be available in Blue and Green colour. Blue colour is going to be selected to connect PC polished SC or LC connectors while green is selected for APC polished connectors.

The fully loaded panel (One height unit or 1U) shall support up to 24 fibres when working with SC Snap-In couplers and up to 48 fibres when working with LC Snap-In couplers.

Unused positions can be populated with optional blank fillers.

Panels are fully painted for a professional look and feel. It t shall be available in both black and white colour.

In the panels, the fibres have to be wired in such a way that the dual OF channel polarity is maintained. Wiring of the fibres has to be done according to the guidelines provided by the manufacturer.

#### Detailed product information

Example of product

LANmark-OF Patch Panel Snap-In Sliding Black

Aginode reference: N439.4SNB

LANmark-OF splice cassette for heat shrink protectors

Aginode reference: N890.090

LANmark-OF splice cassette cover

Aginode reference: N890.092

LANmark-OF splice cassette for Aluminium Protectors

Aginode reference: N890.091

LANmark-OF splice cassette cover

Aginode reference: N890.092

### High density Plug&Play OF patch panel

The ' Plug and Play concept shall be specifically designed for installation in data centres where the high density, integrated patch cord guide and enhanced installation benefits of the patch panel meet the key requirements for implementation.

The patch panel design allows to hold up to 4 MTP/LC modules or adaptor plates in 1U of the distribution rack. Depending on the type of the module a high density of up to 96 fibre connections can be accommodated.

The patch cord guide sits in front of the modules and allows the patch cords to be managed within the same 1U saving expensive rack space. The patch cord guide also provides a labelling facility to identify connections. Additional labelling is provided by printed port numbers on the modules.

The tray shall slide and tilt for improved access to install new modules and adaptor plates.

The patch panel is optimised for installation of MTP/MTP or SC/LC Pre-Term assemblies. The cable glands of the Pre-Term allow a fast and solid fixing of the cable.  There is ample space inside the patch panel to organise the flexible fan-out of the Pre-Term.

Optional Fibre Organiser shall be available to facilitate the installation of the SC/LC Pre-Term.

Up to 4 optional splice cassettes can be installed in the patch panel to accommodate up to 96 splices.

Panels are fully painted in black for a professional look and feel.

Blank fillers are available as separate accessories for unused positions to give a finished look.

The front adaptor plate can be fixed in a flush or recessed position in the rack using the adjustable side brackets.  When the panel is installed recessed the distance between the rack vertical and the rear of the panel is 288 mm.  The front cord management projection is 67 mm. When the panel is installed flush the distance between the rack vertical and the rear of the panel is 248 mm.  The front cord management projection is 107 mm.

#### Detailed product information

Example of product

LANmark-OF Plug&Play Patch Panel Integrated Cord Guide Sliding Black

Aginode reference: N439.3MPP

LANmark-OF fibre organiser 10x

Aginode reference: N890.070

LANmark-OF splice cassette for heat shrink protectors

Aginode reference: N890.090

LANmark-OF splice cassette cover

Aginode reference: N890.092

LANmark-OF splice cassette for Aluminium Protectors

Aginode reference: N890.091

LANmark-OF splice cassette cover

Aginode reference: N890.092

### HD  OF Patch Panel

The High Density (HD) concept is designed for data centres where the high density, integrated patch cord guides and enhanced installation benefits of the HD patch panel meet the key requirements for implementation.

It shall allow quick changes with limited down time, easy migration to other applications and a transition path to parallel optics.

The Aginode’ unique ENSPACE HD 1U panel design has 2 fixed trays. Each tray can have up to 4 ENSPACE modules. The panel can accommodate up to 8 modules allowing 96 LC connections when modules with LC adaptors are used. With LANmark-OF ENSPACE MTP adaptor modules 48 MTP connections within 1U can be installed.  ENSPACE modules need to be ordered separately.

The HD Patch Panels shall be available in 1U and 2U.  The panels are designed for installation inside 19 inch enclosures.

The trays are staggered to facilitate patching and have easier access to the latch of the patch cord.  The trays have printed letters for identification.

On the rear tray 1 cable fixing kit is provided. The slots are suitable for a PG-13 cable gland. The orientation of the fixing kit can be modified to allow for side, angled or rear entry.  An optional third cable fixing kit can be installed on the tray as well.

The patch panel is optimised for installation of the LANmark-OF ENSPACE Pre-Terms: the cable gland of the Pre-Term allows a fast and solid fixing of the cable. There is ample space inside the patch panel to organise the flexible fan-out of the Pre-Terms.

A labelling hinged front cover sits in front of the modules. It can rotate almost 180° even when UHD patch panels are installed underneath. This facilitates port identification when the panel is mounted at the top of the rack.

Panels are fully painted in black for a professional look and feel.

The total depth of the panel is 493mm.  The panels are delivered with the labeling front projection 129mm in front of the rack vertical. The rear of the panel is 364mm recessed compared to the rack vertical. The position of the panel inside the rack can be changed with adjustable side brackets.  It can be moved backwards compared to the rack vertical by 37.5mm or forward by 37,5mm or 75mm.

#### Detailed product information

Example of product

LANmark-OF ENSPACE HD Patch Panel 1U 8x Modules Black

Aginode reference: NSPACE.PPHD1U

Example of product

LANmark-OF ENSPACE HD Patch Panel 2U 16x Modules Black

Aginode reference: NSPACE.PPHD2U

Optional modules and accessories

### UHD  OF Patch Panel

The Ultra High Density (UHD) concept is designed for data centres where the very high density, integrated patch cord guides and enhanced installation benefits of the UHD patch panel meet the key requirements for implementation.

It shall allow quick changes with limited down time, easy migration to other applications and a transition path to 40G/100G.

The UHD system consists of 3 sub-components: Pre-Terms, modules and patch panels.

The patch panel design shall have 3 sliding trays within 1U. Each tray can accommodate up to 4 modules. The panels can be loaded within 1U with up to 12 modules allowing 144 LC connections when modules with LC adaptors are used. With MTP adaptor modules 72 MTP connections within 1U can be installed.  Modules have to be ordered separately.

The UHD Patch Panels shall be available in 1U, 2U and 4U.  The panels are designed for installation inside 19 inch enclosures.

The tray slides shall have 3 locking positions.

The operational position (1)  when the trays are completely in the rack.

The patching position (2) when the tray is moved forward by 75 mm. This allows easy access to the patch cords.

The final stop position (3) before removal of the  tray.

The sliding  trays shall have printed letters to identify the individual trays.  Additional side handles on the left and right sides enhance the pulling forward of the tray.

The UHD Pre-Terms shall be fixed on a separate, sliding and tilting tray located at the rear of the panel. For installation of the cables the tray can be slid out of the patch panel by about 15 cm. This allows easy access to the fixing points for the cables without being in the small space formed by the panel above and underneath when working in a high density rack.

On this rear tray 2 cable fixing kits are provided. The slots are suitable for a PG-13 cable gland. The orientation of the fixing kit can be modified to allow for side, angled or rear entry.  An optional third cable fixing kit can be installed on the tray as well.

The patch panel is optimised for installation of the UHD Pre-Terms: the cable gland of the Pre-Term shall allow a fast and solid fixing of the cable. Ample space is available inside the patch panel to organise the flexible fan-out of the Pre-Terms, including the additional fan-out overlength required to allow the individual trays to slide to the patching or installation position.

A labelling hinged front cover sits in front of the modules. It can rotate almost 180° even when UHD patch panels are installed underneath. This facilitates port identification when the panel is mounted at the top of the rack.

Panels are fully painted in black for a professional look and feel.

The total depth of the panel is 526mm.  The panels are delivered with the labelling front projection 129mm in front of the rack vertical. The rear of the panel is 397mm recessed compared to the rack vertical. The L shaped chassis support brackets can be fitted in 5 different positions to move the position of the panel inside the rack.  It can be moved backwards compared to the rack vertical by 37.5mm or forward by 37,5mm or 75mm.

#### Detailed product information

Example of product

LANmark-OF ENSPACE UHD Patch Panel 1U 12x Modules Black

Aginode reference: NSPACE.PP1U

Example of product

LANmark-OF ENSPACE UHD Patch Panel 2U 12x Modules Black

Aginode reference: NSPACE.PP2U

Example of product

LANmark-OF ENSPACE UHD Patch Panel 4U 12x Modules Black

Aginode reference: NSPACE.PP4U

Optional modules ad accessories

## Maxistrip Optical Fibre pigtails

Fusion spliced pigtails shall be used to terminate both multimode and singlemode fibres.

The use of Maxistrip pigtails is recommended. Maxistrip pigtail is made up of a 250µm coated fibre being loose inside a 900µm tube.

Whenever possible set of 12 coloured pigtails having colours that match the ones of the fibres of the cable shall be selected for easy identification.

Optical performances

Pigtails shall be available with the following types of fibre: OM3, OM4, OM5 and OS2.

Pigtails shall be have Bend Insensitive fibre:

- OM3 compliant to IEC 60793-2-10, fibre model A1a.2b

- OM4 compliant to IEC 60793-2-10, fibre model A1a.3b

- OM5 compliant to IEC 60793-2-10, fibre model A1a.4b

- OS2 compliant to IEC 60793-2-50, fibre model B6.a1

Bend insensitive fibre performances

### Detailed product information

Example of product

## Tight Buffer Optical Fibre pigtails

Fusion spliced pigtails shall be used to terminate both multimode and singlemode fibres.

Tight buffer pigtails are recommended to be used with tight buffer cables, i.e. with 900 um fibres.

Whenever possible set of 12 coloured pigtails having colours that match the ones of the fibres of the cable shall be selected for easy identification.

Optical performances

Pigtails shall be available with the following types of fibre: OM3, OM4, OM5 and OS2.

Pigtails shall be have Bend Insensitive fibre:

- OM3 compliant to IEC 60793-2-10, fibre model A1a.2b

- OM4 compliant to IEC 60793-2-10, fibre model A1a.3b

- OM5 compliant to IEC 60793-2-10, fibre model A1a.4b

- OS2 compliant to IEC 60793-2-50, fibre model B6.a1

Bend insensitive fibre performances

### Detailed product information

Example of product

## OM3 & OM4 BIMMF Optical Fibre Patch cords

The patch cords shall be available in lengths of 1m, 2m, 3m, 5m, 7m, 10m, 15m, 20m, 25m, 30m, 40m and 50m and have a LSHF-FR outer sheath.

The cable shall be flame and fire retardant according to IEC 60332-1.

When using OM3 or OM4 optical fibres, patch cords produced with the same OM3 or OM4 fibre have to be installed.

The patch cords have GIGAliteFLEX fibre inside. This bend insensitive multimode fibre (BIMMF) has a small bend radius of 10mm and is compliant to IEC 60793-2-10, fibre model A1a.2b et 3b.

Duplex LC-LC, duplex LC-SC and duplex SC-SC patch cords have a duplex cable construction with a diameter of 2 X 2.0 mm and short connector boots of 19mm.

A label shall be affixed close to the duplex connector for traceability of the factory measurement results.

Insertion Loss and Return Loss test results shall be available on request.

Patch cord cable is according to IEC 60794-2-50. The colour of Jacket and of the connectors shall be Aqua for both OM3 and OM4 patch cords.

The Fibre Snap-In adapters will be connected to the active equipment OF ports by means of “Cross-over” duplex patch cords in order to maintain the duplex OF channel polarity in accordance with the requirements of ISO/IEC 11801:2017 and EN 50174-1 Ed.3.

The "butterfly" duplex clip allows to easily change the polarity on site by simply removing the 2 connectors and put them in a reverse order back into the same clip. No tool shall be required for this polarity change.

### Detailed product information

Example of products

## OS2 BI Optical Fibre Patch cords

The patch cords shall be available in lengths of 1m, 2m, 3m, 5m, 7m, 10m, 15m, 20m, 25m, 30m, 40m and 50m and have a LSHF-FR outer sheath.

The cable shall be flame and fire retardant according to IEC 60332-1.

UPC polishing performance of the connectors with RL > 50 dB is required.

APC polishing style shall be available with RL > 65 dB.

The patch cords have GIGAliteFLEX fibre inside. This bend insensitive (BI) fibre  has a small bend radius of 10mm and is compliant to ITU-T G.657.A1 and to IEC 60793-2-50, fibre model B6.a1.

Duplex LC-LC, duplex LC-SC and duplex SC-SC patch cords have a duplex cable construction with a diameter of 2 X 2.0 mm and short connector boots of 19mm.

A label shall be affixed close to the duplex connector for traceability of the factory measurement results.

Insertion Loss and Return Loss test results shall be available on request.

The Fibre Snap-In adapters will be connected to the active equipment OF ports by means of “Cross-over” duplex patch cords in order to maintain the duplex OF channel polarity in accordance with the requirements of ISO/IEC 11801:2017 and EN 50174-1 Ed.3.

The "butterfly" duplex clip allows to easily change the polarity on site by simply removing the 2 connectors and put them in a reverse order back into the same clip. No tool shall be required for this polarity change.

### Detailed product information

Example of products

## UHD bend insensitive LC OF Patch cords

The UHD (ultra High Density) patch cords shall be optimised for use in Data Centres environments.

These patch cords shall have a very small bend radius of 10 mm due to the use of bend insensitive fibre and very small diameter of 2 mm.

The round design of the UHD patch cord results in a small bend radius in any direction. Traditional patch cords based on a zipcord design have a bend radius that is dependent on the orientation and are therefore not accepted.

The patch cords shall be available in lengths of 1m, 2m, 3m, 5m, 7m and 10m and have a LSHF-FR outer sheath.

For the support of the advanced high speed Ethernet protocols with stringent power budgets the UHD patch cord features a low loss performance of 0.25 dB. This increases the headroom in the channel and reduces the risk of down time.

CHARACTERISTICS

- Patch cord cable is according to IEC 60794-2-50

- Maximum insertion loss according to IEC 61300-3-4: 0.25 dB

- Typical insertion loss: 0.125 dB

- Bend insensitive fibre

- A label is added close to the uniboot connector for traceability of the factory measurement results

DESIGN

The Fibre Snap-In adapters will be connected to the active equipment OF ports by means of “Cross-over” duplex patch cords in order to maintain the duplex OF channel polarity in accordance with the requirements of ISO/IEC 11801:2017 and EN 50174-1 Ed.3.

The polarity of the patch cord can be changed by opening the uniboot connector on one side and change the position of the 2 LC connectors. A black and yellow plastic square identify the fibre inside the patch cord.  The patch cords are delivered with the black square on the left on side A and the yellow square on the right on side B.  This is required for cross-over or optical crossed patch cords. By changing the position of the black square on side A from the left to the right the patch cord becomes an optical straight patch cord.

The colour of the jacket shall be Aqua for OM4 fibres and Yellow for OS2 fibres.

### Detailed product information

Example of products

## Secure Lock LC port blockers

Port Blockers shall secure the network infrastructure by blocking out unused or unauthorised Duplex LC Adaptors. They also protect the hardware from incoming dust and harmful foreign objects.

LC Port Blockers shall fit into any standard Duplex LC Adaptors without the use of a tool and shall not interfere or lead to the degradation of network performance.

The insertion shall be tool-free onto any standard Duplex LC Adaptors used for outlets and Patch Panels

A dedicated black coloured key must be needed to unlock and remove Port Blockers.

Features

- Exchangeable and re-usable

- Individual packaging for a LANmark-OF Secure Lock - LC Port blockers should contain 100pcs

- Individual packaging for a LANmark-OF Secure Lock LC Port Key should contain 5pcs

- Material: Plastic

- UL Rating: UL94V-2

- RoHS 2 compliant

- Colour of the LC Port Blocker: Transparent Red and Transparent Blue

- Colour of the LC Port Key: Transparent Black

- Operating temperature range: -10°C~60°C

- Storage temperature range: -40°C~68°C

- Humidity: 10%~90%RH

### Detailed product information

Example of products

LANmark Secure Lock LC Port Blockers - Blue

Aginode reference: N124.SLCPBB

LANmark Secure Lock LC Port Blockers - Red

Aginode reference: N124.SLCPBR

LANmark-OF Secure Lock key for LC Port Block key (5pcs)

Aginode reference: N124.SLCPKK

# Inter-Building Backbone Cabling

This backbone will link the active equipment located in the Building Distributors (BD) of every building of the campus to the Data centre through the Campus Distributor (BD).

## Optical Fibre

Refer to former chapter: Intra-building Backbone Cabling

Or Paste here the OM3, OM4, OM5 or OS2 version from the Intra-building Backbone chapter.

## OF cable

Refer to former chapter: Intra-building Backbone Cabling

Or Paste here the OM3, OM4, OM5 or OS2 version from the Intra-building Backbone chapter.

## Optical Fibre Patch Panel

Refer to former chapter: Intra-building Backbone Cabling

## Optical Fibre pigtails

Refer to former chapter: Intra-building Backbone Cabling

## Optical Patch cords

Refer to former chapter: Intra-building Backbone Cabling

# Earthing requirements

Earthing shall be implemented according to EN 50174-2:2018 Ed.3 & EN 50310:2016/A1:2020 standards and to local relevant regulations.

The method of achieving all earth connections at the same safe potential is to bond them together and physically connect them in the soil or ground at the same point i.e. the MET.

This is known as equipotential bonding. The MET (Main Earthing Terminal) shall be provided by the local electricity supplier as a drilled copper bus-bar and sized in accordance with local wiring regulations, existing building requirements and future growth expectations.

This procedure applies to unshielded, shielded and fibre optic cabling systems alike. All metal parts regardless of the type of cabling must be earthed for personnel safety reasons and to avoid potential damage to equipment.

All metallic parts of the system (mainly cabinets and patch panels) shall be bonded throughout back to a local (Secondary) Bonding Busbar (SBB) usually located in the cabling distributors rooms / computer room. All those SBBs are linked back to the MET (Main Earthing Terminal) bonding point.  The bonding network will normally be provided by the local Electricity supplier in accordance with country-specific wiring regulations.

The metal frame of the Patch Panel must not be bonded to the cabinet with a separate bond connection if the patch panels automatically make contact with the 19” metal frame of the Cabinets.

The bonding bar of the cabinet must be connected to the local SBB. The dimension of the bonding conductor is 6mm².

If racks are adjacent to each other they shall not be bonded together using a daisy chaining structure.

Every rack has to be directly connected to the local bonding bar (SBB) or to the main bonding backbone conductor circulating in the room.

Main bond runs back to the local SBB shall utilise larger bonding conductor.

Earth runs should be kept as short as practically possible, with the wire as straight as is practically possible.
Please refer to local bonding regulation documents in order to ensure that the bonding conductors are sized accordingly.

If no or only a poor protective bonding system is present in the building, a separate bonding conductor to the MET of the building is required. The dimensions of the conductor should then be 16mm².

# Testing

The manufacturer of the cabling system shall provide copper (Data) and optical fibre testing procedures that

clearly describes the tools and settings to be used to ensure correct measurements of the system.

## Data Copper Testing

100 % of the installed horizontal links have to be tested in accordance with IEC 61935-1 and with the field testing procedure of the manufacturer.

Link testing is required in accordance with the updated EN 50174 Ed.3 cabling standard.

Channel testing is only permitted if the actual cords used to create the channel are used and installed in the as-built configuration.

The cabling system shall to be tested against ISO Class E, EA, FA link limits. (Keep the right class only)

The measurements shall be done using Level IV testing equipment.

The testing equipment must be yearly calibrated by the manufacturer and the copy of the calibration certificate must be included in the warranty request.

The following parameters have to be tested:

- Wire-map

- Continuity

- Signal conductors

- Screen conductors (if present)

- Short circuits

- Open circuits

- Length

- Internal transmission Return loss

- Insertion loss

- Pair-to-pair NEXT

- PSNEXT

- Pair-to-pair ACR-N

- PSACR-N

- Pair-to-pair ACR-F

- PSACR-F

- Direct current (d.c.) loop resistance

- Propagation delay

- Delay skew

The PSANEXT, PSANEXTavg, PSAACR-F, and PSAACR-Favg (A-NEXT and A-ELFEXT) don’t have to be tested for screened cabling systems. The conformance to those Alien crosstalk parameters is met by design for screened systems in accordance with ISO11801.

The complete test results of all the installed channels have to be collected in a certification file. It is preferred to have the test result in electronic format to facilitate the certification procedure.

Apart from all the test results mentioned above, a few more documents have to be added to the file:  a list of material used for the project, a design of the network, a Cable schedule per distributor and finally all the necessary co-ordinates of the persons responsible of the project.

## Fibre testing

In order to avoid contamination and potential damage of optical fibre end-faces and/or connecting hardware

due to the build-up of static charge during transport, manufacturers recommended cleaning procedures (compliant to the ISO 62627 standard – Fibre optic connector cleaning methods) shall be applied before any connection is made to any fibre connector.

Although pre-terminated assemblies (LC or MTP) are supplied with test certificates, it is a requirement under the manufacturer warranty procedure to supply test results for the installed system and applies for both Multimode and  Singlemode installations.

The testing procedure shall comply with the ISO/IEC 14763-3:2006/A1 2009 and IEC 61280-4-1/Ed.3 and IEC 61280-4-2/Ed.2 standards and be in accordance with the latest issue of the ‘Field testing procedure’ document to be provided by the cabling manufacturer.

The ISO/IEC 14763 standard specifies the implementation and operation of customer premises cabling.

The part 3 of this ISO document (14763-3) details test procedures for optical fibre cabling designed in accordance with ISO/IEC 11801: 2017 ed.3 and installed according to the recommendations of ISO/IEC 14763-2 (Planning and installation of customer premises cabling).

For Multimode fibres, the test procedure is based on the use of the “one-jumper method” specified by Method 2 of IEC 61280-4-1. This procedure is used for testing links for which the connector loss is a significant portion of the total link attenuation. This is the case for LAN premises links.

For singlemode fibres, the test procedure to be applied is the same and is based on the use of the “one-jumper method” specified by Method 1a of IEC 61280-4-2.

Fibre-optic Tests applied to links and exclude equipment and work area cord.

All 100 % of the installed OF links have to be tested and must pass the acceptance criteria.

Test cords shall be equipped with reference connectors and ISO 14763-3:2006 limits shall be selected on the tester.

The attenuation of the link is measured using the insertion loss method. This method uses an optical source and an optical power meter to compare the difference between two optical power levels.

When testing multimode optical fibre links with a Light Source and a Power Meter, this measurement equipment has to be capable of operating at

- 850nm and 1300nm for multimode fibres (OM3, OM4 & OM5)

- 1310nm and 1550nm for singlemode fibres (OS2)

Encircled Flux compliance shall be provided through the use of a Modal Controller Device that is either integrated into the test equipment (light source), or an external device.

The test scenario with an OTDR shall be one of the following for each link:

- Dual direction @ 850nm and @ 1300nm for multimode fibres

- Dual direction @ 1310nm and @ 1550nm for singlemode fibres

The use of launch and receiving reels is required. (Refer to manufacturer testing procedure)

The use of certification tool is recommended. Those tools are capable of producing a report logging the time of the test the link identification under test, the link length, the attenuation at the window tested and the acceptable link attenuation. The report shall also identify in which direction the testing was implemented.

when testing with basic optical source and power meter, the operator will fill up a report logging

- the time of the test,

- the link identification under test,

- the link length and attenuation at the window tested.

- The report shall also identify in which direction the testing was implemented.

- Acceptable link attenuation (To be calculated)

The measured attenuation of the links shall have a lower value than the acceptable link attenuation calculated.

The testing equipment must be yearly calibrated by the manufacturer and the copy of the calibration certificate must be included in the warranty request.

# Procedures

## Installation Guide

All the components have to be installed according to the procedures prescribed by the supplier. During the whole period of installation, the installer has to put an Installation Guide at the disposal of the client, so that he can verify the compliance of the installation to the guidelines of the supplier.

## Fire Protection

The installer has to closely follow the local regulations concerning fire protection.

The integrity of the fire barrier has to be maintained or restored.

Where fire-stopping compounds are used to restore integrity around data cables , they must be to an approved material so as not to damage the cable.(Cable manufacturer can advise approved compounds).

## Earthing

For the earthing of all the proposed products, the installer has to closely follow the related recommendations of the supplier, in accordance with local regulations. The earthing procedure that has to be followed shall be put at the disposal by the supplier under an official document.

# Management of the Project

## Design of the Project and labelling

The vendor will first make a site survey. This will allow him to propose a complete turnkey solution without any additional costs for unforeseen labour. If possible, the installer will try to use the existing infrastructure as much as possible. If cable supports or cable trays are lacking, then the vendor will have to evaluate the necessary quantities and price and take up a detailed description in his offer.

To ensure the transparency of the installation and the maintenance of the structured cabling, the vendor has to develop a numbering and labelling scheme in agreement with the owner or his representative in order to identify all the components without ambiguity. After the temporary reception of the project, all the cabinets’ layouts and the drawings of the building will be completed referring to this numbering scheme.

## Project Management

For the complete duration of the project the vendor will appoint a Project Manager, who will work on his behalf. He will be the single point of contact to ensure a smooth co-ordination.

For project with an estimated duration over 2 weeks, the vendor will appoint a Site Manager, who will be permanently present on site on behalf of the vendor. The Site Manager will report to the Project Manager, in order to ensure that the correct information is communicated from the commencement of the project until the hand-over of the network to the client

# Warranty

The following copper and fibre sub-system warranties apply to both standard AND AIM products.

Telecommunications contractor must register the project and submit test data for approval, per the requirements of the cabling manufacturer certification program guidelines.

Once approved, the manufacturer will extend a 25-year Warranty to the end user.

Copper and fibre patch cords are considered as replaceable items and are specifically excluded from the 25 year product guarantee due to the normal wear and tear that can occur.

## Copper sub-system

### Cat.6 sub-system

The manufacturer must guarantee to the End User that the products referenced within the specific Warranty Modules (Class E System) when correctly installed in accordance with installation guidelines:

- Will be free from product defects in materials and workmanship

- Are guaranteed to exceed the Class E Channel and Permanent Link requirements as specified in ISO/IEC 11801: 2017 ed.3

- Supports the following application (not limited):

• 10baseT Ethernet

• 100baseT Fast Ethernet

• 1000baseTX Gigabit Ethernet

• 155Mbit ATM

• 1.2Gbit ATM

- For a duration of 25 years

All components including the patch cords have to be produced by the same cabling system manufacturer to ensure warranted performances and applications against the standards.

### Cat.6A sub-system

The manufacturer must guarantee to the End User that the products referenced within the specific Warranty Modules (Class EA System) when correctly installed in accordance with installation guidelines:

- Will be free from product defects in materials and workmanship

- Are guaranteed to exceed

- Class EA Channel and Permanent Link as specified in ISO/IEC 11801: 2017 ed.3

- Augmented Cat 6 Link and Channel requirements as specified in ANSI/TIA -568.2-D: 2018

- Supports the following application (not limited):

• 10baseT Ethernet

• 100baseTX Fast Ethernet

• 1000baseTX Gigabit Ethernet

• 10G base-T Ethernet IEEE 802.3an

• 155Mbit ATM

• 1200Mbit ATM

• POE type 1 to 4

- For a duration of 25 years

- Provide a guaranteed headroom

• of at least 10 dB on A-NEXT

• of at least 15 dB on A-ELFEXT

All components including the Cat6A patch cords have to be produced by the same cabling system manufacturer to ensure warranted performances and applications against the standards.

### Cat.7A sub-system

The manufacturer must guarantee to the End User that the products referenced within the specific Warranty Modules (Class FA System) when correctly installed in accordance with installation guidelines:

- Will be free from product defects in materials and workmanship

- Are guaranteed to exceed the Class FA Channel and Category 7A mated component requirements as specified in ISO/IEC 11801: 2017 ed.3

- Supports the following application (not limited):

• 10baseT - Ethernet

• 100baseTX - Fast Ethernet

• 1000MbaseTX - Gigabit Ethernet

• 10GBaseT – 10Gigabit Ethernet over copper

• 25GBASE-T Ethernet (IEEE 802.3bq draft) Maximum Channel length 30 Meters

• 155Mbit ATM

• 1.2 Gbit ATM

• POE type 1 to 4

- For a duration of 25 years

Class FA Channel performance is only warranted when Cat.7A patch cords are used and these have not been subjected to any damage which can occur due to normal wear & tear.

Due to the backwards compatibility of Cat.7A/8 GG45 connector it is possible to use Cat.5e, Cat.6 and Cat.6A patch cords.

In this case the following Channel performance shall be warranted:

- Class EA using Cat.6A patch cords

- Class E using Cat.6 patch cords

- Class D using Cat.5e patch cords

All components including the patch cords have to be produced by the same cabling system manufacturer to ensure warranted performances and applications against the standards.

To ensure correct installation in accordance with the guidelines, the installer shall attend to a specific Cat.7A installation training organised by the manufacturer.

The warranty will only be issued if the installer has received the official Cat.7A installation training certificate from the cabling system manufacturer.

## Fibre sub-system

### OM3 sub-system

The manufacturer must guarantee to the End User that the products referenced within the specific Warranty Modules (OM3 pre-terminated fibre System) when correctly installed in accordance with installation guidelines:

- Will be free from product defects in materials and workmanship

- support any current or future application designed to be supported by fibres according to  IEC 60793-2-10 A1a.2b

Fibre systems are warranted for 25 years.

Guaranteed distances vary depending on the number of connections and shall comply to the following table:

All components including the patch cords  and pigtails have to be produced by the same cabling system manufacturer to ensure warranted performances and applications distances against the standards.

### OM4 sub-system

The manufacturer must guarantee to the End User that the products referenced within the specific Warranty Modules (OM4 pre-terminated fibre System) when correctly installed in accordance with installation guidelines:

- Will be free from product defects in materials and workmanship

- support any current or future application designed to be supported by fibres according to  IEC 60793-2-10 A1a.3b

Fibre systems are warranted for 25 years.

Guaranteed distances vary depending on the number of connections and shall comply to the following table:

All components including the patch cords  and pigtails have to be produced by the same cabling system manufacturer to ensure warranted performances and applications distances against the standards.

manufacturer to ensure warranted performances and applications distances against the standards.

### OM5 sub-system

The manufacturer must guarantee to the End User that the products referenced within the specific Warranty Modules (OM5 pre-terminated fibre System) when correctly installed in accordance with installation guidelines:

- Will be free from product defects in materials and workmanship

- support any current or future application designed to be supported by fibres according to  IEC 60793-2-10 A1a.4b

Fibre systems are warranted for 25 years.

Guaranteed distances vary depending on the number of connections and shall comply to the following table:

All components including the patch cords  and pigtails have to be produced by the same cabling system manufacturer to ensure warranted performances and applications distances against the standards.

### OS2 sub-system

The manufacturer must guarantee to the End User that the products referenced within the specific Warranty Modules (OS2 pre-terminated fibre System) when correctly installed in accordance with installation guidelines:

- Will be free from product defects in materials and workmanship

- support any current or future application designed to be supported by Singlemode G657.A1 fibres

Fibre systems are warranted for 25 years.

Guaranteed distances vary depending on the number of connections and shall comply to the following table:

All components including the patch cords  and pigtails have to be produced by the same cabling system manufacturer to ensure warranted performances and applications distances against the standards.

# Documentation

## Response inclusions to the bid price

- Datasheets of the proposed components

- Table with the guaranteed values for the proposed twisted pair and FO cables

- Detailed warranty conditions

- Certificate of Approved/Certified Installer granted by the supplier

- Schedule of execution with the expected start and end dates

- Summarised plan of the cabling design philosophy + cabinets layouts that have to be submitted to the customer for approval.

## During the Presentation of the Offer

- Presentation of the proposed products

- Technical justification of the backbone concept

## Kick-off of the Project

- Installation guide of the supplier

- Schedule of execution in agreement with the customer

## On completion of the installation

- Certification file

- 25-year “Link & Channel Warranty” delivered by the supplier

- Plans “as built”

Disclaimer

This document is intended to be used as technical guidelines to develop specific requirements for LAN cabling Systems.

Aginode reserves the right to change the technical specifications at any time without notice.

The user should review the information to ensure conformity to the current applicable standards and to the project requirements.

Aginode assumes no liability due to the use of these specifications and is not responsible for any error or omission.